## Cover
Monte Carlo Calculation of PFDavg
Author: | Stephen L. Thomas
Last Updated: | 2020-09-27
Purpose: | This spreadsheet demonstrates using Monte Carlo simulation to incorporate uncertainty into Safety Integrity Level (SIL) calculations for Safety Instrumented Systems (SIS) designed per IEC 61511
Disclaimer: | This spreadsheet is supplied for information only and is provided as-is with no warranty either express or implied. No claim is made for its suitability for any specific engineering purpose. Users should evaluate its suitability for their application or consult a qualified engineering professional.
License: | Released into the Public Domain. Please cite the original author if reposting.
More Information: | Connect with the author at the locations below:
https://www.linkedin.com/in/stephenlthomas/
https://sisengineer.com
https://functionalsafetyengineer.com

## Model
Monte Carlo Calculation of PFDavg
Expand for directions
General 1) Cells highlighted in yellow are intended to be edited to define the parameters of the calculation 2) For this example, we are using a very simple form of simplified SIL equations. These can be modified, but be sure to modify in both the point estimate cells (B25-27) and the Monte Carlo cells (G49+, O49+, W49+) 3) We did not do MC for common cause or mission time, but these could be added Procedure: 1) Set your desired confidence level (typically 70%, 90%, or 95%) and mission time 2) Adjust the parameters to define distributions for failure rate, proof test interval, and proof test coverage (see SISEngineer.com for help on how to do this) 3) That's it. The Monte Carlo simulation will generate a predicted distribution for PFDavg
General Parameters
Confidence Limit | 70% |  | Adjustable Parameters
Mission Time (yr) | 20
Component Distributons and Parameters
|  | Gamma parameters |  |  |  | Lognormal Parameters |  |  |  | Beta Parameters
Component | Lambda | alpha | beta |  | PT Interval | mu | sigma |  | PT Coverage | alpha | beta
Sensor | 9.2816e-07 | 2 | 2628000 |  | 19435.9574 | 9.77 | 0.2 |  | 89.85% | 32 | 5
Logic Solver | 1.0459e-07 | 1.5 | 17520000 |  | 48770.4611 | 10.69 | 0.2 |  | 93.55% | 40 | 4
Final Element | 1.5532e-06 | 4 | 3066000 |  | 48770.4611 | 10.69 | 0.2 |  | 94.96% | 36 | 3
PDF Graphs
The Monte Carlo will draw from these distributions. For brevity, not all of the PDFs are shown as graphs
Beta Distribution Fit
[22 empty] | Mean | 0.053045
[22 empty] | Variance | 0.00049774
[20 empty] | Plotting the Beta distribution |  | alpha | 5.3002
[13 empty] | Monte Carlo Results | [8 empty] | Beta | 94.6188
PFDavg Point Values | 70% | [11 empty] | Mean PFDavg: | 0.053045
Sensor | 0.024609 |  | Point values using basic simplified equations and the specified upper confidence limit for each variable. They are provided for comparison to MC results. They should not be wildly different. |  |  |  | Skip to the Monte Carlo Results | [5 empty] | 70% Confidence: | 0.06233
Logic Solver | 0.0035673 | [11 empty] | 90% Confidence: | 0.082986 | [8 empty] | We can estimate a Beta distribution to fit the Monte Carlo results
Final Element | 0.049689 | [11 empty] | 95% Confidence: | 0.094146
PFDavg Total | 0.077864
Details of Monte Carlo Simulation
The MC simulation draws a uniformly distributed random probability using RAND() and then uses the inverse cumulative distribution function to calculate the corresponding random variable (e.g. Lambda). This is repeated a large number of times. If everything is working, the histograms below should be the same shape as the probability density functions above. (Note: the histograms and PDFs for PT interval and coverage are not shown.)
Sensor | [7 empty] | Logic Solver | [6 empty] | Final Element | [7 empty] | System
Probability | Lambda | Probability | PT Interval | Probability | PT Coverage | PFDavg |  | Probability | Lambda | Probability | PT Interval | Probability | PT Coverage | PFDavg | Probability | Lambda | Probability | PT Interval | Probability | PT Coverage | PFDavg |  | Total PFDavg
0.083805 | 1.8214e-07 | 0.51553 | 17637.5705 | 0.76158 | 0.90724 | 0.0029373 |  | 0.79543 | 1.3094e-07 | 0.32258 | 40050.7383 | 0.39965 | 0.90418 | 0.0034698 | 0.29456 | 8.9341e-07 | 0.14251 | 35460.5159 | 0.50553 | 0.93081 | 0.020159 |  | 0.026566
0.40135 | 5.2523e-07 | 0.33916 | 16107.633 | 0.47178 | 0.86751 | 0.0097654 |  | 0.12324 | 1.9544e-08 | 0.13924 | 35356.9871 | 0.54197 | 0.91962 | 0.00045536 | 0.90017 | 2.1799e-06 | 0.80385 | 52108.8789 | 0.38221 | 0.91739 | 0.06788 |  | 0.0781
0.52201 | 6.6577e-07 | 0.36564 | 16339.0863 | 0.10993 | 0.79399 | 0.016333 |  | 0.31247 | 4.2159e-08 | 0.18078 | 36589.5596 | 0.35368 | 0.89862 | 0.0010675 | 0.49077 | 1.1834e-06 | 0.064462 | 32413.4208 | 0.83066 | 0.96255 | 0.022342 |  | 0.039743
0.057853 | 1.469e-07 | 0.21689 | 14964.7668 | 0.47453 | 0.8679 | 0.0026539 |  | 0.21707 | 3.0701e-08 | 0.088535 | 33524.5604 | 0.25718 | 0.88521 | 0.00076426 | 0.96581 | 2.7122e-06 | 0.56867 | 45460.3558 | 0.66335 | 0.9461 | 0.071132 |  | 0.07455
0.49849 | 6.3681e-07 | 0.18445 | 14622.1663 | 0.10805 | 0.79328 | 0.015225 |  | 0.80237 | 1.3327e-07 | 0.80018 | 51971.6945 | 0.3504 | 0.8982 | 0.0042991 | 0.97518 | 2.8629e-06 | 0.010469 | 27672.0136 | 0.84115 | 0.96369 | 0.04728 |  | 0.066804
0.59169 | 7.578e-07 | 0.64345 | 18836.2765 | 0.93581 | 0.93946 | 0.010724 |  | 0.86169 | 1.5712e-07 | 0.85819 | 54417.5156 | 0.37195 | 0.90088 | 0.0052156 | 0.39738 | 1.0436e-06 | 0.77888 | 51209.6947 | 0.61977 | 0.94197 | 0.030474 |  | 0.046413
0.41209 | 5.3706e-07 | 0.75552 | 20098.3027 | 0.33029 | 0.84593 | 0.011814 |  | 0.61965 | 8.7729e-08 | 0.011847 | 27933.7014 | 0.73718 | 0.93936 | 0.001617 | 0.057607 | 4.6763e-07 | 0.71186 | 49107.3337 | 0.65591 | 0.9454 | 0.013092 |  | 0.026523
0.91752 | 1.5717e-06 | 0.85826 | 21687.9194 | 0.74343 | 0.90461 | 0.028551 |  | 0.19194 | 2.7735e-08 | 0.59831 | 46156.6581 | 0.32458 | 0.89486 | 0.00082824 | 0.49205 | 1.1854e-06 | 0.97202 | 64361.6084 | 0.29433 | 0.90607 | 0.044316 |  | 0.073696
0.6009 | 7.7081e-07 | 0.077306 | 13164.9563 | 0.8193 | 0.91609 | 0.010314 |  | 0.20582 | 2.9373e-08 | 0.75733 | 50490.7764 | 0.017206 | 0.79914 | 0.0011094 | 0.25922 | 8.4084e-07 | 0.76478 | 50734.1696 | 0.58733 | 0.93887 | 0.024528 |  | 0.035952
0.43938 | 5.676e-07 | 0.5537 | 17979.7439 | 0.45006 | 0.86442 | 0.011152 |  | 0.37 | 4.9409e-08 | 0.42803 | 42349.9297 | 0.76867 | 0.94269 | 0.0012343 | 0.7923 | 1.7768e-06 | 0.66216 | 47747.0237 | 0.57084 | 0.93728 | 0.04952 |  | 0.061906
0.90654 | 1.5124e-06 | 0.38367 | 16495.267 | 0.13517 | 0.8027 | 0.036152 |  | 0.66992 | 9.7862e-08 | 0.37722 | 41251.4429 | 0.89589 | 0.9582 | 0.0022924 | 0.20236 | 7.5289e-07 | 0.30317 | 39613.9919 | 0.36537 | 0.91536 | 0.019232 |  | 0.057677
0.13919 | 2.4797e-07 | 0.13553 | 14042.9493 | 0.91414 | 0.93402 | 0.0030594 |  | 0.61904 | 8.7613e-08 | 0.0027959 | 25231.2871 | 0.45239 | 0.91016 | 0.0016955 | 0.11963 | 6.0878e-07 | 0.0062259 | 26640.4205 | 0.52969 | 0.93324 | 0.011128 |  | 0.015883
0.67623 | 8.8698e-07 | 0.82506 | 21098.6018 | 0.70238 | 0.89884 | 0.016271 |  | 0.65617 | 9.4963e-08 | 0.36649 | 41017.9434 | 0.72999 | 0.93862 | 0.0023387 | 0.98147 | 2.9979e-06 | 0.65002 | 47433.0552 | 0.10113 | 0.86633 | 0.096699 |  | 0.11531
0.11849 | 2.2436e-07 | 0.56705 | 18101.9027 | 0.070306 | 0.77624 | 0.0059741 |  | 0.34697 | 4.6464e-08 | 0.18593 | 36731.8407 | 0.47885 | 0.91302 | 0.0011332 | 0.90487 | 2.205e-06 | 0.1902 | 36848.4831 | 0.10664 | 0.86814 | 0.06074 |  | 0.067847
0.4575 | 5.8833e-07 | 0.32751 | 16004.6981 | 0.73491 | 0.90339 | 0.0092322 |  | 0.64498 | 9.2679e-08 | 0.24811 | 38326.9494 | 0.82554 | 0.94907 | 0.0020991 | 0.54935 | 1.2763e-06 | 0.17979 | 36562.0421 | 0.4754 | 0.92771 | 0.029727 |  | 0.041058
0.24257 | 3.5809e-07 | 0.78948 | 20556.2561 | 0.68979 | 0.8971 | 0.0065295 |  | 0.42124 | 5.6208e-08 | 0.56431 | 45359.7057 | 0.92695 | 0.96315 | 0.0014092 | 0.5152 | 1.2215e-06 | 0.5139 | 44221.6053 | 0.78608 | 0.95794 | 0.030372 |  | 0.038311
0.857 | 1.3068e-06 | 0.3104 | 15852.0491 | 0.56623 | 0.88047 | 0.022803 |  | 0.19256 | 2.7809e-08 | 0.99808 | 78297.7664 | 0.10728 | 0.85352 | 0.0012861 | 0.048171 | 4.4008e-07 | 0.23261 | 37946.8281 | 0.066174 | 0.85232 | 0.01281 |  | 0.036899
0.61472 | 7.9075e-07 | 0.50602 | 17553.6222 | 0.27717 | 0.8365 | 0.017131 |  | 0.0042526 | 1.8347e-09 | 0.13624 | 35260.6642 | 0.39984 | 0.90421 | 4.4644e-05 | 0.9868 | 3.1521e-06 | 0.40263 | 41801.538 | 0.56888 | 0.93709 | 0.079109 |  | 0.096285
0.7451 | 1.0145e-06 | 0.43177 | 16909.4438 | 0.79826 | 0.91276 | 0.015582 |  | 0.17782 | 2.6069e-08 | 0.23769 | 38072.6247 | 0.25604 | 0.88503 | 0.00070176 | 0.46369 | 1.142e-06 | 0.57649 | 45642.0745 | 0.092004 | 0.86314 | 0.036187 |  | 0.05247
0.58149 | 7.4365e-07 | 0.93029 | 23519.6647 | 0.51531 | 0.87356 | 0.015876 |  | 0.89156 | 1.7312e-07 | 0.91831 | 58032.3112 | 0.82095 | 0.94853 | 0.0055452 | 0.5644 | 1.3011e-06 | 0.45441 | 42920.1133 | 0.86839 | 0.96676 | 0.030781 |  | 0.052203
0.18376 | 2.9651e-07 | 0.17777 | 14548.1398 | 0.49951 | 0.87139 | 0.0052201 |  | 0.9764 | 2.7039e-07 | 0.90987 | 57411.2979 | 0.92708 | 0.96317 | 0.0083482 | 0.62213 | 1.4012e-06 | 0.019838 | 29102.5184 | 0.9025 | 0.97097 | 0.02336 |  | 0.036928
0.14556 | 2.5507e-07 | 0.75889 | 20141.7239 | 0.9293 | 0.93773 | 0.0038002 |  | 0.32734 | 4.4001e-08 | 0.48121 | 43502.5986 | 0.97964 | 0.97567 | 0.0010276 | 5.2816e-05 | 6.3997e-08 | 0.86935 | 54976.6051 | 0.10832 | 0.86867 | 0.0022644 |  | 0.0070921
0.3792 | 5.0115e-07 | 0.82589 | 21112.2325 | 0.33284 | 0.84636 | 0.011222 |  | 0.68514 | 1.012e-07 | 0.82966 | 53133.7652 | 0.35772 | 0.89912 | 0.0033115 | 0.45911 | 1.1351e-06 | 0.91183 | 57550.8014 | 0.091123 | 0.86282 | 0.041824 |  | 0.056358
0.15778 | 2.6852e-07 | 0.46861 | 17227.2596 | 0.54809 | 0.87802 | 0.0049 |  | 0.0057205 | 2.2421e-09 | 0.47615 | 43392.2172 | 0.044687 | 0.82609 | 7.4343e-05 | 0.52209 | 1.2324e-06 | 0.86498 | 54753.2234 | 0.82361 | 0.9618 | 0.036573 |  | 0.041547
0.57145 | 7.2997e-07 | 0.56602 | 18092.4715 | 0.033679 | 0.74951 | 0.020967 |  | 0.94848 | 2.2112e-07 | 0.93899 | 59830.8153 | 0.65379 | 0.93088 | 0.0074965 | 0.13867 | 6.4467e-07 | 0.57133 | 45522.0204 | 0.61029 | 0.94107 | 0.017137 |  | 0.0456
0.27084 | 3.8734e-07 | 0.67421 | 19154.8979 | 0.69986 | 0.89849 | 0.0067776 |  | 0.60824 | 8.5591e-08 | 0.67083 | 47975.4016 | 0.95515 | 0.96874 | 0.0022233 | 0.89134 | 2.1354e-06 | 0.88856 | 56037.676 | 0.42888 | 0.92272 | 0.069662 |  | 0.078663
0.54062 | 6.8937e-07 | 0.29455 | 15708.7744 | 0.68746 | 0.89679 | 0.011089 |  | 0.17443 | 2.5668e-08 | 0.047177 | 31427.1291 | 0.15944 | 0.86717 | 0.00064843 | 0.26501 | 8.4953e-07 | 0.27362 | 38933.7962 | 0.052899 | 0.84521 | 0.025497 |  | 0.037234
0.80518 | 1.1527e-06 | 0.20396 | 14831.2051 | 0.89098 | 0.92898 | 0.015111 |  | 0.39235 | 5.2329e-08 | 0.27372 | 38936.2558 | 0.07831 | 0.84328 | 0.0015775 | 0.56732 | 1.306e-06 | 0.578 | 45677.3325 | 0.55366 | 0.93561 | 0.035272 |  | 0.051961
0.47544 | 6.0927e-07 | 0.61526 | 18557.1183 | 0.042318 | 0.75752 | 0.017224 |  | 0.96074 | 2.3838e-07 | 0.55023 | 45037.3625 | 0.032516 | 0.81683 | 0.0082097 | 0.81242 | 1.8357e-06 | 0.048271 | 31496.4227 | 0.02296 | 0.82003 | 0.052648 |  | 0.078081
0.42032 | 5.4618e-07 | 0.80012 | 20710.7284 | 0.21446 | 0.82367 | 0.013095 |  | 0.56322 | 7.7636e-08 | 0.46658 | 43183.9475 | 0.75409 | 0.94114 | 0.001978 | 0.77544 | 1.7309e-06 | 0.046667 | 31394.4857 | 0.94916 | 0.97799 | 0.02991 |  | 0.044983
0.87333 | 1.3661e-06 | 0.47406 | 17274.4535 | 0.461 | 0.86599 | 0.026255 |  | 0.22942 | 3.2161e-08 | 0.79609 | 51820.8357 | 0.86626 | 0.95411 | 0.00092436 | 0.26038 | 8.4258e-07 | 0.46471 | 43143.3694 | 0.8699 | 0.96694 | 0.020015 |  | 0.047194
0.70591 | 9.3882e-07 | 0.14747 | 14193.3275 | 0.097062 | 0.7889 | 0.022617 |  | 0.5271 | 7.1725e-08 | 0.018105 | 28885.3326 | 0.12348 | 0.85826 | 0.0017797 | 0.45524 | 1.1293e-06 | 0.91002 | 57421.7699 | 0.78077 | 0.95741 | 0.035256 |  | 0.059652
0.71497 | 9.5551e-07 | 0.039008 | 12302.2499 | 0.20027 | 0.8204 | 0.019855 |  | 0.59524 | 8.3219e-08 | 0.00099418 | 23661.5567 | 0.43353 | 0.90806 | 0.0015642 | 0.82036 | 1.8604e-06 | 0.48776 | 43645.7602 | 0.25795 | 0.90067 | 0.052754 |  | 0.074173
0.64377 | 8.3455e-07 | 0.46318 | 17180.206 | 0.48987 | 0.87005 | 0.015738 |  | 0.99067 | 3.2802e-07 | 0.76977 | 50900.0949 | 0.10393 | 0.85246 | 0.011356 | 0.63249 | 1.4201e-06 | 0.40534 | 41860.2694 | 0.55661 | 0.9359 | 0.035793 |  | 0.062886
0.43013 | 5.5716e-07 | 0.31158 | 15862.7069 | 0.82177 | 0.91649 | 0.0081258 |  | 0.096284 | 1.621e-08 | 0.77619 | 51117.4429 | 0.22032 | 0.87914 | 0.00053586 | 0.1441 | 6.5452e-07 | 0.33689 | 40368.6323 | 0.55159 | 0.9354 | 0.016061 |  | 0.024723
0.45635 | 5.8701e-07 | 0.74716 | 19992.5591 | 0.10317 | 0.79138 | 0.015371 |  | 0.49394 | 6.6607e-08 | 0.33679 | 40366.3202 | 0.88137 | 0.95614 | 0.0015413 | 0.78736 | 1.763e-06 | 0.58477 | 45835.9371 | 0.50654 | 0.93092 | 0.048283 |  | 0.065196
0.78251 | 1.0966e-06 | 0.24694 | 15262.7474 | 0.4002 | 0.85707 | 0.020903 |  | 0.27942 | 3.813e-08 | 0.84929 | 53996.7905 | 0.050891 | 0.82997 | 0.0014224 | 0.87949 | 2.0803e-06 | 0.17037 | 36295.9835 | 0.71097 | 0.95062 | 0.044888 |  | 0.067213
0.42781 | 5.5456e-07 | 0.05591 | 12733.4503 | 0.095176 | 0.78811 | 0.013076 |  | 0.33535 | 4.5002e-08 | 0.49623 | 43831.6047 | 0.33122 | 0.89574 | 0.0012944 | 0.48747 | 1.1783e-06 | 0.9447 | 60421.2436 | 0.25682 | 0.90049 | 0.042326 |  | 0.056696
0.12925 | 2.3674e-07 | 0.61422 | 18547.0221 | 0.13163 | 0.80156 | 0.0058751 |  | 0.90703 | 1.8315e-07 | 0.68017 | 48225.1949 | 0.39562 | 0.90371 | 0.0055357 | 0.87718 | 2.0701e-06 | 0.20279 | 37184.8684 | 0.92121 | 0.97354 | 0.042268 |  | 0.053678
0.24497 | 3.6057e-07 | 0.6573 | 18977.7022 | 0.098386 | 0.78945 | 0.0093514 |  | 0.76527 | 1.2157e-07 | 0.27108 | 38874.253 | 0.012113 | 0.7898 | 0.004105 | 0.65427 | 1.4611e-06 | 0.90908 | 57355.5226 | 0.49908 | 0.93016 | 0.047914 |  | 0.06137
0.53777 | 6.8571e-07 | 0.9442 | 24057.6841 | 0.11827 | 0.79703 | 0.018766 |  | 0.71439 | 1.0803e-07 | 0.17457 | 36415.3381 | 0.031587 | 0.816 | 0.0033462 | 0.64696 | 1.4472e-06 | 0.80337 | 52090.9385 | 0.022617 | 0.81959 | 0.053763 |  | 0.075875
0.78694 | 1.1072e-06 | 0.60668 | 18474.2926 | 0.7117 | 0.90013 | 0.018892 |  | 0.074364 | 1.3386e-08 | 0.15138 | 35735.3776 | 0.35097 | 0.89828 | 0.00033413 | 0.43816 | 1.1037e-06 | 0.070798 | 32729.2734 | 0.53492 | 0.93376 | 0.023271 |  | 0.042497
0.96954 | 2.0312e-06 | 0.38216 | 16482.2046 | 0.23061 | 0.8272 | 0.044594 |  | 0.61018 | 8.5951e-08 | 0.27549 | 38977.4604 | 0.24806 | 0.88377 | 0.0023555 | 0.39016 | 1.033e-06 | 0.54163 | 44842.4302 | 0.5639 | 0.93661 | 0.027429 |  | 0.074379
0.087652 | 1.8704e-07 | 0.83778 | 21313.0869 | 0.97695 | 0.95431 | 0.0026508 |  | 0.99115 | 3.3131e-07 | 0.49152 | 43728.167 | 0.9232 | 0.9625 | 0.0080604 | 0.63319 | 1.4214e-06 | 0.28663 | 39235.8646 | 0.46059 | 0.92615 | 0.035021 |  | 0.045732
0.36986 | 4.9112e-07 | 0.38607 | 16516.0257 | 0.93604 | 0.93953 | 0.006412 |  | 0.39966 | 5.3298e-08 | 0.40931 | 41945.9588 | 0.11076 | 0.85458 | 0.0016342 | 0.25723 | 8.3784e-07 | 0.32102 | 40015.7999 | 0.59094 | 0.93922 | 0.020206 |  | 0.028252
0.71432 | 9.5429e-07 | 0.30154 | 15772.1964 | 0.032751 | 0.74855 | 0.026654 |  | 0.84853 | 1.511e-07 | 0.83009 | 53151.6212 | 0.9178 | 0.9616 | 0.0043696 | 0.72682 | 1.6121e-06 | 0.19693 | 37029.6443 | 0.39626 | 0.91903 | 0.038865 |  | 0.069888
0.9931 | 2.6878e-06 | 0.48772 | 17393.3593 | 0.61489 | 0.88699 | 0.047342 |  | 0.063149 | 1.1881e-08 | 0.93499 | 59444.5969 | 0.73224 | 0.93885 | 0.00039519 | 0.0032882 | 1.9453e-07 | 0.27966 | 39074.5686 | 0.14576 | 0.87907 | 0.0054018 |  | 0.053139
0.14385 | 2.5317e-07 | 0.063927 | 12906.3723 | 0.89509 | 0.92983 | 0.0030753 |  | 0.93938 | 2.1072e-07 | 0.45201 | 42868.0856 | 0.60346 | 0.92584 | 0.0055507 | 0.15791 | 6.7895e-07 | 0.6222 | 46735.1129 | 0.90622 | 0.97146 | 0.01711 |  | 0.025736
0.26504 | 3.8134e-07 | 0.26194 | 15406.1907 | 0.98935 | 0.96246 | 0.0040813 |  | 0.39306 | 5.2422e-08 | 0.52014 | 44360.359 | 0.29936 | 0.89143 | 0.0015351 | 0.42617 | 1.0859e-06 | 0.82153 | 52798.8549 | 0.75116 | 0.95449 | 0.031693 |  | 0.03731
0.62942 | 8.1259e-07 | 0.17105 | 14472.3703 | 0.41994 | 0.86003 | 0.01502 |  | 0.19963 | 2.8643e-08 | 0.17955 | 36555.4491 | 0.63896 | 0.9294 | 0.00066371 | 0.18549 | 7.2554e-07 | 0.12553 | 34907.0844 | 0.24657 | 0.89887 | 0.01781 |  | 0.033495
0.94499 | 1.7611e-06 | 0.61952 | 18598.6792 | 0.52816 | 0.87532 | 0.033569 |  | 0.84753 | 1.5065e-07 | 0.84751 | 53915.0774 | 0.76827 | 0.94265 | 0.0045852 | 0.68405 | 1.52e-06 | 0.61008 | 46439.538 | 0.18046 | 0.88687 | 0.046366 |  | 0.08452
0.65258 | 8.484e-07 | 0.65873 | 18992.5291 | 0.94075 | 0.94085 | 0.011976 |  | 0.91692 | 1.9044e-07 | 0.80357 | 52098.4216 | 0.013524 | 0.7927 | 0.0073907 | 0.89847 | 2.1711e-06 | 0.12417 | 34861.0854 | 0.099797 | 0.86588 | 0.058275 |  | 0.077641
0.173 | 2.8501e-07 | 0.028782 | 11970.4953 | 0.19227 | 0.81849 | 0.005928 |  | 0.88081 | 1.6692e-07 | 0.31796 | 39947.4503 | 0.55541 | 0.92099 | 0.0042259 | 0.53974 | 1.2606e-06 | 0.019979 | 29119.5458 | 0.1145 | 0.87058 | 0.030271 |  | 0.040425
0.57822 | 7.3918e-07 | 0.72209 | 19688.9782 | 0.93164 | 0.93834 | 0.010821 |  | 0.44018 | 5.8821e-08 | 0.41773 | 42127.7094 | 0.32126 | 0.89442 | 0.0016522 | 0.92952 | 2.3585e-06 | 0.85755 | 54386.7872 | 0.7161 | 0.95111 | 0.071101 |  | 0.083574
0.80124 | 1.1425e-06 | 0.83069 | 21192.0144 | 0.47892 | 0.86852 | 0.023674 |  | 0.71548 | 1.0829e-07 | 0.30995 | 39767.3051 | 0.84273 | 0.95113 | 0.0025116 | 0.12126 | 6.1195e-07 | 0.44082 | 42626.0101 | 0.51235 | 0.9315 | 0.015821 |  | 0.042007
0.43978 | 5.6806e-07 | 0.56485 | 18081.6572 | 0.071455 | 0.77686 | 0.015094 |  | 0.69169 | 1.0267e-07 | 0.49706 | 43849.8006 | 0.79065 | 0.94509 | 0.0026214 | 0.21077 | 7.6628e-07 | 0.47673 | 43404.8115 | 0.50356 | 0.93061 | 0.020134 |  | 0.037849
0.1784 | 2.9079e-07 | 0.80414 | 20770.7895 | 0.73662 | 0.90363 | 0.0051837 |  | 0.23093 | 3.234e-08 | 0.97645 | 65322.7056 | 0.71266 | 0.93683 | 0.0011685 | 0.8911 | 2.1342e-06 | 0.45117 | 42849.9656 | 0.1997 | 0.89068 | 0.061164 |  | 0.067516
0.71733 | 9.5994e-07 | 0.61569 | 18561.3431 | 0.27269 | 0.83565 | 0.021265 |  | 0.77595 | 1.2476e-07 | 0.50702 | 44069.4006 | 0.54123 | 0.91955 | 0.003407 | 0.31038 | 9.1664e-07 | 0.29952 | 39531.0732 | 0.068895 | 0.85362 | 0.027219 |  | 0.051891
0.99308 | 2.6863e-06 | 0.010117 | 10999.52 | 0.49287 | 0.87047 | 0.043342 |  | 0.63048 | 8.981e-08 | 0.54259 | 44864.1303 | 0.38179 | 0.90207 | 0.0025878 | 0.49373 | 1.1879e-06 | 0.48125 | 43503.5008 | 0.75703 | 0.95506 | 0.029355 |  | 0.075285
0.23357 | 3.4875e-07 | 0.64672 | 18869.3779 | 0.79465 | 0.9122 | 0.0056839 |  | 0.88653 | 1.7015e-07 | 0.24854 | 38337.5105 | 0.96368 | 0.97081 | 0.0036015 | 0.36383 | 9.9458e-07 | 0.32085 | 40012.0439 | 0.10431 | 0.86738 | 0.028813 |  | 0.038098
0.19421 | 3.0759e-07 | 0.45909 | 17144.8962 | 0.47692 | 0.86824 | 0.0058397 |  | 0.13823 | 2.1358e-08 | 0.21684 | 37549.4862 | 0.67944 | 0.93346 | 0.00049881 | 0.43889 | 1.1048e-06 | 0.59733 | 46133.1353 | 0.51602 | 0.93187 | 0.030342 |  | 0.03668
0.51878 | 6.6173e-07 | 0.068169 | 12991.9675 | 0.37015 | 0.85243 | 0.012219 |  | 0.56864 | 7.8556e-08 | 0.88927 | 56079.5898 | 0.7388 | 0.93953 | 0.0024856 | 0.57362 | 1.3165e-06 | 0.80022 | 51973.0692 | 0.71642 | 0.95114 | 0.038175 |  | 0.05288
0.10028 | 2.027e-07 | 0.78489 | 20491.4008 | 0.72811 | 0.90243 | 0.0036067 |  | 0.35629 | 4.7649e-08 | 0.77448 | 51058.857 | 0.89511 | 0.95809 | 0.0013404 | 0.8992 | 2.1748e-06 | 0.49622 | 43831.3054 | 0.76261 | 0.95561 | 0.054004 |  | 0.058951
0.35654 | 4.7689e-07 | 0.28295 | 15602.3633 | 0.88868 | 0.92852 | 0.0064406 |  | 0.73078 | 1.1213e-07 | 0.11775 | 34639.1653 | 0.47987 | 0.91313 | 0.0026266 | 0.77603 | 1.7324e-06 | 0.76042 | 50591.1239 | 0.98381 | 0.98596 | 0.045339 |  | 0.054406
0.97223 | 2.0729e-06 | 0.99597 | 29731.1196 | 0.10992 | 0.79398 | 0.061877 |  | 0.33084 | 4.4437e-08 | 0.89687 | 56544.6639 | 0.030863 | 0.81533 | 0.0017432 | 0.4198 | 1.0765e-06 | 0.29066 | 39328.7134 | 0.85042 | 0.96471 | 0.02375 |  | 0.08737
0.25534 | 3.7131e-07 | 0.25897 | 15378.0107 | 0.69882 | 0.89835 | 0.0058713 |  | 0.6729 | 9.8503e-08 | 0.54154 | 44840.2117 | 0.80544 | 0.94675 | 0.0025504 | 0.67538 | 1.5025e-06 | 0.67144 | 47991.4547 | 0.55186 | 0.93543 | 0.042224 |  | 0.050646
0.028068 | 9.816e-08 | 0.96098 | 24895.0709 | 0.040897 | 0.75631 | 0.0030196 |  | 0.31089 | 4.1965e-08 | 0.63684 | 47098.8346 | 0.41147 | 0.90556 | 0.0012421 | 0.66919 | 1.4902e-06 | 0.15724 | 35911.8816 | 0.9689 | 0.98193 | 0.028632 |  | 0.032894
0.25359 | 3.695e-07 | 0.08478 | 13296.7672 | 0.47157 | 0.86748 | 0.0064202 |  | 0.63411 | 9.0519e-08 | 0.85664 | 54342.6436 | 0.31792 | 0.89397 | 0.0030395 | 0.88167 | 2.0901e-06 | 0.35479 | 40762.3195 | 0.26912 | 0.90238 | 0.056312 |  | 0.065772
0.14654 | 2.5616e-07 | 0.79445 | 20627.6718 | 0.84941 | 0.92115 | 0.004203 |  | 0.99514 | 3.6816e-07 | 0.75946 | 50559.8849 | 0.41752 | 0.90625 | 0.011458 | 0.40357 | 1.0526e-06 | 0.61564 | 46574.6431 | 0.93103 | 0.975 | 0.026205 |  | 0.041866
0.2018 | 3.1559e-07 | 0.4455 | 17027.5821 | 0.37963 | 0.85391 | 0.006333 |  | 0.95207 | 2.2572e-07 | 0.61856 | 46645.7812 | 0.82112 | 0.94855 | 0.0060109 | 0.45154 | 1.1238e-06 | 0.55801 | 45215.1295 | 0.47684 | 0.92786 | 0.030674 |  | 0.043018
0.76925 | 1.0662e-06 | 0.21724 | 14968.353 | 0.75285 | 0.90596 | 0.016012 |  | 0.50451 | 6.8209e-08 | 0.02113 | 29255.119 | 0.39683 | 0.90385 | 0.0014763 | 0.30533 | 9.0923e-07 | 0.76692 | 50804.8569 | 0.56074 | 0.9363 | 0.026699 |  | 0.044187
0.069179 | 1.6281e-07 | 0.95844 | 24750.0086 | 0.45899 | 0.8657 | 0.0036597 |  | 0.7476 | 1.1659e-07 | 0.7754 | 51090.439 | 0.47398 | 0.9125 | 0.0036114 | 0.24091 | 8.1309e-07 | 0.52712 | 44516.0301 | 0.80876 | 0.96025 | 0.02021 |  | 0.027481
0.16743 | 2.79e-07 | 0.60012 | 18411.5109 | 0.685 | 0.89645 | 0.0048333 |  | 0.057762 | 1.1139e-08 | 0.52781 | 44531.5607 | 0.67866 | 0.93338 | 0.0002965 | 0.032198 | 3.854e-07 | 0.4603 | 43047.6538 | 0.79235 | 0.95857 | 0.0093503 |  | 0.01448
0.58881 | 7.5378e-07 | 0.13631 | 14052.9643 | 0.29697 | 0.84014 | 0.015006 |  | 0.19146 | 2.768e-08 | 0.036076 | 30649.368 | 0.90951 | 0.96027 | 0.00050367 | 0.76209 | 1.6964e-06 | 0.30593 | 39676.6342 | 0.46305 | 0.92641 | 0.042113 |  | 0.057622
0.20518 | 3.1914e-07 | 0.59583 | 18370.7424 | 0.41981 | 0.86001 | 0.0064347 |  | 0.98155 | 2.8576e-07 | 0.85578 | 54301.4497 | 0.23988 | 0.88245 | 0.0097893 | 0.45289 | 1.1258e-06 | 0.42129 | 42204.3983 | 0.24202 | 0.89813 | 0.031382 |  | 0.047606
0.99971 | 4.0266e-06 | 0.52265 | 17700.7336 | 0.96598 | 0.94932 | 0.051707 |  | 0.68292 | 1.007e-07 | 0.34883 | 40631.7622 | 0.18525 | 0.87262 | 0.0029089 | 0.69083 | 1.534e-06 | 0.1153 | 34552.6267 | 0.24801 | 0.8991 | 0.037387 |  | 0.092003
0.17709 | 2.8939e-07 | 0.58419 | 18260.9963 | 0.4504 | 0.86447 | 0.0057198 |  | 0.018089 | 4.9212e-09 | 0.08492 | 33371.457 | 0.964 | 0.9709 | 9.227e-05 | 0.87264 | 2.0506e-06 | 0.52177 | 44396.7447 | 0.57813 | 0.93799 | 0.053837 |  | 0.059649
0.041678 | 1.2208e-07 | 0.54247 | 17878.0977 | 0.10558 | 0.79233 | 0.0030857 |  | 0.43564 | 5.8189e-08 | 0.18437 | 36689.1319 | 0.47146 | 0.91223 | 0.0014212 | 0.020559 | 3.3431e-07 | 0.63043 | 46938.8383 | 0.36727 | 0.9156 | 0.0096556 |  | 0.014162
0.23555 | 3.5081e-07 | 0.76467 | 20217.0049 | 0.55061 | 0.87836 | 0.0068528 |  | 0.46801 | 6.2779e-08 | 0.16146 | 36037.1512 | 0.83261 | 0.94991 | 0.00135 | 0.42153 | 1.0791e-06 | 0.80269 | 52065.3309 | 0.97649 | 0.9838 | 0.029167 |  | 0.03737
0.093413 | 1.9426e-07 | 0.32394 | 15973.0195 | 0.5883 | 0.88343 | 0.0033544 |  | 0.16117 | 2.4097e-08 | 0.72556 | 49508.0299 | 0.5916 | 0.92465 | 0.00071059 | 0.88961 | 2.127e-06 | 0.57494 | 45605.8946 | 0.4197 | 0.9217 | 0.059294 |  | 0.063359
0.78718 | 1.1077e-06 | 0.72554 | 19729.6155 | 0.61602 | 0.88714 | 0.020646 |  | 0.95678 | 2.3228e-07 | 0.3454 | 40556.3464 | 0.41359 | 0.9058 | 0.0061832 | 0.58593 | 1.3374e-06 | 0.044355 | 31243.0387 | 0.59516 | 0.93962 | 0.026705 |  | 0.053534
0.42057 | 5.4646e-07 | 0.43963 | 16977.0995 | 0.51873 | 0.87403 | 0.010084 |  | 0.18938 | 2.7433e-08 | 0.81402 | 52499.6845 | 0.8307 | 0.94968 | 0.00080482 | 0.22152 | 7.8316e-07 | 0.030973 | 30232.1939 | 0.71349 | 0.95086 | 0.014628 |  | 0.025517
0.15518 | 2.6568e-07 | 0.31922 | 15931.0217 | 0.39958 | 0.85698 | 0.0051422 |  | 0.9242 | 1.9637e-07 | 0.067142 | 32549.4777 | 0.93979 | 0.96551 | 0.0036788 | 0.98086 | 2.9831e-06 | 0.15412 | 35818.405 | 0.36288 | 0.91506 | 0.071083 |  | 0.079904
0.97206 | 2.0701e-06 | 0.89525 | 22493.584 | 0.17121 | 0.81314 | 0.052817 |  | 0.63961 | 9.1604e-08 | 0.47286 | 43320.6902 | 0.87083 | 0.95471 | 0.0022578 | 0.37425 | 1.0098e-06 | 0.50039 | 43923.1317 | 0.56998 | 0.9372 | 0.026339 |  | 0.081413
0.62721 | 8.0926e-07 | 0.34529 | 16161.5117 | 0.94221 | 0.94127 | 0.010319 |  | 0.39384 | 5.2526e-08 | 0.94701 | 60676.0226 | 0.91266 | 0.96076 | 0.0017115 | 0.01705 | 3.155e-07 | 0.23186 | 37928.2079 | 0.76368 | 0.95571 | 0.0069422 |  | 0.018972
0.51686 | 6.5935e-07 | 0.37094 | 16385.0972 | 0.21857 | 0.82458 | 0.014586 |  | 0.63756 | 9.1198e-08 | 0.92502 | 58567.7282 | 0.66348 | 0.93185 | 0.0030331 | 0.62133 | 1.3997e-06 | 0.76221 | 50649.6872 | 0.92779 | 0.97451 | 0.03767 |  | 0.055289
0.47271 | 6.0605e-07 | 0.1047 | 13615.3839 | 0.8327 | 0.9183 | 0.0081264 |  | 0.59132 | 8.2517e-08 | 0.13861 | 35336.9582 | 0.26028 | 0.88569 | 0.0021176 | 0.70099 | 1.5553e-06 | 0.59769 | 46141.7617 | 0.26631 | 0.90196 | 0.045723 |  | 0.055967
0.78987 | 1.1142e-06 | 0.084674 | 13294.9526 | 0.058686 | 0.76942 | 0.028205 |  | 0.15272 | 2.3092e-08 | 0.68794 | 48436.3007 | 0.5085 | 0.91616 | 0.00068196 | 0.80198 | 1.8045e-06 | 0.32233 | 40044.986 | 0.00090259 | 0.7356 | 0.068374 |  | 0.097262
0.62244 | 8.0214e-07 | 0.50186 | 17517.0674 | 0.056714 | 0.76815 | 0.021688 |  | 0.33395 | 4.4826e-08 | 0.5162 | 44272.7369 | 0.95622 | 0.96899 | 0.0010833 | 0.68315 | 1.5182e-06 | 0.84803 | 53938.859 | 0.98637 | 0.98684 | 0.042156 |  | 0.064928
0.89363 | 1.4505e-06 | 0.67936 | 19209.9293 | 0.83422 | 0.91855 | 0.023146 |  | 0.39655 | 5.2885e-08 | 0.61545 | 46569.9922 | 0.30279 | 0.8919 | 0.0015991 | 0.89106 | 2.134e-06 | 0.3807 | 41327.1111 | 0.17513 | 0.88576 | 0.060414 |  | 0.08516
0.033076 | 1.074e-07 | 0.071132 | 13049.663 | 0.84 | 0.91953 | 0.0014015 |  | 0.80954 | 1.3577e-07 | 0.59525 | 46083.5745 | 0.49489 | 0.91473 | 0.0038757 | 0.94881 | 2.5174e-06 | 0.68656 | 48398.6532 | 0.0072334 | 0.78789 | 0.094772 |  | 0.10005
0.18571 | 2.9858e-07 | 0.37273 | 16400.6005 | 0.17681 | 0.81461 | 0.0068436 |  | 0.0076877 | 2.7399e-09 | 0.55081 | 45050.6826 | 0.12694 | 0.8592 | 8.6822e-05 | 0.93993 | 2.4385e-06 | 0.055383 | 31921.9245 | 0.48868 | 0.92909 | 0.051308 |  | 0.058238
0.23895 | 3.5434e-07 | 0.5669 | 18100.576 | 0.81047 | 0.91468 | 0.0055818 |  | 0.54771 | 7.5052e-08 | 0.62645 | 46840.112 | 0.29875 | 0.89134 | 0.0022811 | 0.063593 | 4.8387e-07 | 0.38048 | 41322.3362 | 0.63207 | 0.94314 | 0.011839 |  | 0.019702
0.9957 | 2.8922e-06 | 0.66977 | 19107.9129 | 0.8942 | 0.92965 | 0.043512 |  | 0.88711 | 1.7049e-07 | 0.2184 | 37589.4814 | 0.10122 | 0.85159 | 0.0049451 | 0.85598 | 1.9838e-06 | 0.79744 | 51870.4767 | 0.5763 | 0.93781 | 0.059057 |  | 0.10751
0.43667 | 5.6454e-07 | 0.33743 | 16092.3878 | 0.56346 | 0.8801 | 0.0099274 |  | 0.97805 | 2.7494e-07 | 0.95514 | 61658.7708 | 0.24634 | 0.8835 | 0.010295 | 0.57708 | 1.3224e-06 | 0.087415 | 33477.5446 | 0.22337 | 0.89498 | 0.031975 |  | 0.052197
0.26664 | 3.83e-07 | 0.60237 | 18433.0011 | 0.45564 | 0.86522 | 0.007576 |  | 0.90917 | 1.8466e-07 | 0.52853 | 44547.7508 | 0.29114 | 0.89026 | 0.005437 | 0.93696 | 2.4145e-06 | 0.7968 | 51846.983 | 0.046269 | 0.84103 | 0.086265 |  | 0.099278
0.901 | 1.4849e-06 | 0.52933 | 17760.2034 | 0.74921 | 0.90544 | 0.02424 |  | 0.15461 | 2.3317e-08 | 0.61296 | 46509.2783 | 0.97457 | 0.97393 | 0.00058134 | 0.25447 | 8.3367e-07 | 0.67163 | 47996.6296 | 0.3604 | 0.91476 | 0.024527 |  | 0.049348
0.14615 | 2.5572e-07 | 0.63868 | 18788.2074 | 0.31202 | 0.8428 | 0.0055461 |  | 0.33435 | 4.4876e-08 | 0.93589 | 59529.6526 | 0.31194 | 0.89316 | 0.001613 | 0.98501 | 3.0945e-06 | 0.75724 | 50487.9908 | 0.63157 | 0.94309 | 0.0891 |  | 0.096259
0.92651 | 1.6261e-06 | 0.18925 | 14674.5277 | 0.261 | 0.8334 | 0.033674 |  | 0.98256 | 2.8928e-07 | 0.81936 | 52711.3161 | 0.54477 | 0.91991 | 0.0090432 | 0.33075 | 9.4641e-07 | 0.88052 | 55576.4317 | 0.12283 | 0.87302 | 0.033487 |  | 0.076205
0.0030437 | 3.049e-08 | 0.82433 | 21086.7933 | 0.55113 | 0.87843 | 0.00060708 |  | 0.11189 | 1.8154e-08 | 0.15767 | 35924.7766 | 0.76963 | 0.9428 | 0.00039841 | 0.22316 | 7.8571e-07 | 0.32167 | 40030.2985 | 0.46049 | 0.92614 | 0.019648 |  | 0.020654
0.40595 | 5.3029e-07 | 0.75132 | 20044.848 | 0.57413 | 0.88153 | 0.010188 |  | 0.24917 | 3.4505e-08 | 0.99389 | 72483.292 | 0.99722 | 0.98638 | 0.0012747 | 0.3192 | 9.2955e-07 | 0.6761 | 48115.7613 | 0.70591 | 0.95014 | 0.025308 |  | 0.036771
0.023474 | 8.9071e-08 | 0.60233 | 18432.5989 | 0.15091 | 0.8075 | 0.0021649 |  | 0.29259 | 3.9726e-08 | 0.35811 | 40835.0239 | 0.23413 | 0.8815 | 0.0011274 | 0.59351 | 1.3505e-06 | 0.03062 | 30201.5696 | 0.13702 | 0.87687 | 0.03245 |  | 0.035742
0.49266 | 6.2977e-07 | 0.80114 | 20725.8513 | 0.68271 | 0.89614 | 0.011578 |  | 0.94477 | 2.1668e-07 | 0.83954 | 53557.8023 | 0.021582 | 0.80532 | 0.0083683 | 0.87795 | 2.0735e-06 | 0.16673 | 36190.9779 | 0.33104 | 0.91104 | 0.050341 |  | 0.070288
0.89818 | 1.4715e-06 | 0.05803 | 12780.7385 | 0.43735 | 0.86258 | 0.025824 |  | 0.86489 | 1.5867e-07 | 0.15314 | 35788.6609 | 0.29519 | 0.89084 | 0.0040466 | 0.64144 | 1.4368e-06 | 0.11974 | 34708.6116 | 0.14265 | 0.8783 | 0.037217 |  | 0.067088
0.75998 | 1.0458e-06 | 0.90047 | 22625.8469 | 0.17803 | 0.81493 | 0.026596 |  | 0.24904 | 3.4489e-08 | 0.29809 | 39498.6673 | 0.72182 | 0.93777 | 0.00082677 | 0.20637 | 7.5929e-07 | 0.91295 | 57632.1182 | 0.91656 | 0.97288 | 0.02309 |  | 0.050513
0.19701 | 3.1054e-07 | 0.12455 | 13897.8631 | 0.48864 | 0.86988 | 0.0054169 |  | 0.092136 | 1.5685e-08 | 0.17854 | 36527.0728 | 0.18602 | 0.87277 | 0.00042484 | 0.09202 | 5.5191e-07 | 0.27891 | 39057.304 | 0.9336 | 0.9754 | 0.011702 |  | 0.017544
0.8911 | 1.4392e-06 | 0.1445 | 14156.6345 | 0.24672 | 0.83055 | 0.029825 |  | 0.030569 | 7.0876e-09 | 0.21256 | 37439.5948 | 0.60603 | 0.9261 | 0.00016876 | 0.25976 | 8.4165e-07 | 0.56383 | 45348.6386 | 0.87424 | 0.96745 | 0.020862 |  | 0.050856
0.17326 | 2.8529e-07 | 0.4412 | 16990.5659 | 0.76523 | 0.90777 | 0.0045049 |  | 0.8877 | 1.7083e-07 | 0.74951 | 50241.254 | 0.28127 | 0.88884 | 0.0054779 | 0.075535 | 5.1401e-07 | 0.18694 | 36759.4818 | 0.22103 | 0.89457 | 0.013199 |  | 0.023181
0.20262 | 3.1645e-07 | 0.7956 | 20644.5017 | 0.44843 | 0.86419 | 0.0065878 |  | 0.78505 | 1.2758e-07 | 0.99221 | 71236.1869 | 0.61362 | 0.92686 | 0.0050291 | 0.25591 | 8.3585e-07 | 0.041163 | 31024.4339 | 0.7885 | 0.95818 | 0.015486 |  | 0.027103
0.87845 | 1.3861e-06 | 0.94582 | 24127.8399 | 0.20795 | 0.82219 | 0.035339 |  | 0.41383 | 5.5201e-08 | 0.82451 | 52920.2662 | 0.35872 | 0.89925 | 0.0018007 | 0.053169 | 4.5501e-07 | 0.43032 | 42399.3599 | 0.8398 | 0.96354 | 0.010748 |  | 0.047887
0.94471 | 1.7587e-06 | 0.61054 | 18511.4132 | 0.057012 | 0.76834 | 0.048196 |  | 0.4245 | 5.6654e-08 | 0.037014 | 30721.2867 | 0.4343 | 0.90815 | 0.0012461 | 0.73581 | 1.6327e-06 | 0.419 | 42155.0596 | 0.6283 | 0.94278 | 0.040628 |  | 0.090071
0.30401 | 4.2173e-07 | 0.090956 | 13400.1603 | 0.83034 | 0.9179 | 0.0056266 |  | 0.32992 | 4.4323e-08 | 0.4879 | 43648.8341 | 0.12737 | 0.85932 | 0.0013775 | 0.3614 | 9.9104e-07 | 0.17433 | 36408.705 | 0.33151 | 0.91111 | 0.024155 |  | 0.031159
0.6679 | 8.7315e-07 | 0.58606 | 18278.5827 | 0.66208 | 0.89333 | 0.015287 |  | 0.53751 | 7.339e-08 | 0.23462 | 37996.85 | 0.88956 | 0.95729 | 0.0016093 | 0.90752 | 2.2197e-06 | 0.75746 | 50495.0656 | 0.23269 | 0.89658 | 0.070356 |  | 0.087253
0.88904 | 1.4302e-06 | 0.82683 | 21127.8001 | 0.5963 | 0.8845 | 0.027833 |  | 0.003985 | 1.756e-09 | 0.81681 | 52609.487 | 0.90275 | 0.95922 | 5.0579e-05 | 0.499 | 1.1961e-06 | 0.90643 | 57171.6431 | 0.91472 | 0.97262 | 0.036124 |  | 0.064008
0.93367 | 1.6741e-06 | 0.25887 | 15377.068 | 0.097372 | 0.78903 | 0.041094 |  | 0.82268 | 1.4057e-07 | 0.070772 | 32728.0015 | 0.75785 | 0.94154 | 0.0028858 | 0.76329 | 1.6994e-06 | 0.83434 | 53331.8615 | 0.74855 | 0.95423 | 0.050057 |  | 0.094036
0.31763 | 4.3592e-07 | 0.27587 | 15536.8487 | 0.81968 | 0.91615 | 0.0063043 |  | 0.26399 | 3.6276e-08 | 0.052431 | 31750.2307 | 0.85312 | 0.95242 | 0.00069968 | 0.25854 | 8.3981e-07 | 0.42996 | 42391.5471 | 0.068017 | 0.85321 | 0.025986 |  | 0.03299
0.78405 | 1.1003e-06 | 0.28433 | 15615.0831 | 0.17687 | 0.81463 | 0.024865 |  | 0.43002 | 5.7412e-08 | 0.39957 | 41735.4886 | 0.85235 | 0.95232 | 0.0013807 | 0.81478 | 1.8429e-06 | 0.72282 | 49426.6581 | 0.59269 | 0.93939 | 0.05257 |  | 0.078816
0.54361 | 6.9322e-07 | 0.48126 | 17337.089 | 0.22078 | 0.82507 | 0.015581 |  | 0.53467 | 7.2933e-08 | 0.30469 | 39648.5409 | 0.082851 | 0.84508 | 0.0022116 | 0.034232 | 3.9312e-07 | 0.0043972 | 26004.1295 | 0.84537 | 0.96415 | 0.0061627 |  | 0.023955
0.99658 | 2.9904e-06 | 0.072148 | 13069.0847 | 0.56429 | 0.88021 | 0.048581 |  | 0.11125 | 1.8076e-08 | 0.53499 | 44692.6374 | 0.48935 | 0.91414 | 0.00050521 | 0.66012 | 1.4724e-06 | 0.41469 | 42061.9965 | 0.19603 | 0.88998 | 0.04175 |  | 0.090836
0.24147 | 3.5695e-07 | 0.26563 | 15441.0592 | 0.26778 | 0.83471 | 0.0074688 |  | 0.0068348 | 2.5296e-09 | 0.7164 | 49238.736 | 0.37678 | 0.90146 | 7.7976e-05 | 0.95147 | 2.5435e-06 | 0.32019 | 39997.3701 | 0.94066 | 0.97653 | 0.054902 |  | 0.062449
0.82984 | 1.2207e-06 | 0.59241 | 18338.3336 | 0.75853 | 0.90679 | 0.020117 |  | 0.38389 | 5.1216e-08 | 0.15396 | 35813.4937 | 0.13571 | 0.8615 | 0.0014115 | 0.55219 | 1.2809e-06 | 0.5371 | 44740.0835 | 0.83262 | 0.96276 | 0.031765 |  | 0.053293
0.30026 | 4.1783e-07 | 0.12337 | 13881.8598 | 0.19118 | 0.81822 | 0.0090264 |  | 0.12587 | 1.9865e-08 | 0.24419 | 38231.8096 | 0.91574 | 0.96126 | 0.00043244 | 0.25944 | 8.4117e-07 | 0.50803 | 44091.7287 | 0.72233 | 0.9517 | 0.021208 |  | 0.030666
0.14832 | 2.5813e-07 | 0.2714 | 15495.1331 | 0.87686 | 0.92618 | 0.0035214 |  | 0.98502 | 2.9873e-07 | 0.36691 | 41027.2876 | 0.95584 | 0.9689 | 0.0067513 | 0.55805 | 1.2906e-06 | 0.4051 | 41855.0953 | 0.73525 | 0.95295 | 0.031057 |  | 0.04133
0.1539 | 2.6427e-07 | 0.11487 | 13763.8241 | 0.95484 | 0.94522 | 0.0029871 |  | 0.19311 | 2.7874e-08 | 0.65005 | 47433.907 | 0.29281 | 0.8905 | 0.00085606 | 0.5783 | 1.3244e-06 | 0.73221 | 49707.1936 | 0.86519 | 0.96639 | 0.03571 |  | 0.039553
0.046072 | 1.2913e-07 | 0.15494 | 14284.1703 | 0.19138 | 0.81827 | 0.0028104 |  | 0.37168 | 4.9626e-08 | 0.3169 | 39923.5727 | 0.94952 | 0.9675 | 0.0010997 | 0.77146 | 1.7204e-06 | 0.15848 | 35948.9669 | 0.64676 | 0.94453 | 0.037568 |  | 0.041479
0.32322 | 4.4177e-07 | 0.14452 | 14156.8222 | 0.051472 | 0.76458 | 0.011501 |  | 0.25886 | 3.5662e-08 | 0.43659 | 42534.6583 | 0.77037 | 0.94288 | 0.00089356 | 0.89161 | 2.1367e-06 | 0.36858 | 41063.5873 | 0.56059 | 0.93628 | 0.053 |  | 0.065395
0.74502 | 1.0143e-06 | 0.51223 | 17608.4169 | 0.47382 | 0.8678 | 0.019495 |  | 0.47151 | 6.3287e-08 | 0.18361 | 36668.0378 | 0.24991 | 0.88406 | 0.0016685 | 0.97088 | 2.7881e-06 | 0.69759 | 48703.0157 | 0.0028075 | 0.76334 | 0.10963 |  | 0.13079
0.32202 | 4.4052e-07 | 0.15027 | 14227.741 | 0.90294 | 0.93151 | 0.0055622 |  | 0.82315 | 1.4075e-07 | 0.60426 | 46299.0953 | 0.36561 | 0.9001 | 0.0041646 | 0.74518 | 1.6549e-06 | 0.048168 | 31489.9425 | 0.70418 | 0.94997 | 0.032005 |  | 0.041731
0.23295 | 3.4811e-07 | 0.42919 | 16887.2474 | 0.22154 | 0.82524 | 0.0077549 |  | 0.32592 | 4.3824e-08 | 0.11473 | 34532.1047 | 0.90655 | 0.9598 | 0.00088056 | 0.36442 | 9.9544e-07 | 0.58918 | 45939.785 | 0.39433 | 0.91881 | 0.028089 |  | 0.036724
0.17105 | 2.8291e-07 | 0.085167 | 13303.3862 | 0.98714 | 0.96065 | 0.0027829 |  | 0.089233 | 1.5316e-08 | 0.76394 | 50706.4094 | 0.88131 | 0.95613 | 0.00043012 | 0.23763 | 8.0806e-07 | 0.32053 | 40004.8904 | 0.7076 | 0.9503 | 0.018878 |  | 0.022091
0.35407 | 4.7427e-07 | 0.16572 | 14411.1793 | 0.83653 | 0.91894 | 0.0065082 |  | 0.90486 | 1.8165e-07 | 0.40629 | 41880.6606 | 0.65929 | 0.93143 | 0.0046341 | 0.42746 | 1.0878e-06 | 0.60449 | 46304.7299 | 0.012573 | 0.80293 | 0.039002 |  | 0.050145
0.14736 | 2.5707e-07 | 0.04257 | 12402.814 | 0.12046 | 0.7978 | 0.0058252 |  | 0.53335 | 7.2721e-08 | 0.57125 | 45520.1375 | 0.94696 | 0.96696 | 0.0018109 | 0.43798 | 1.1035e-06 | 0.79083 | 51630.054 | 0.31751 | 0.90926 | 0.034673 |  | 0.042309
0.73425 | 9.9258e-07 | 0.53642 | 17823.7059 | 0.97559 | 0.95361 | 0.012469 |  | 0.78759 | 1.2839e-07 | 0.23598 | 38030.3091 | 0.92276 | 0.96243 | 0.0027721 | 0.71125 | 1.5774e-06 | 0.20861 | 37337.4082 | 0.018757 | 0.8142 | 0.049651 |  | 0.064892
0.65681 | 8.5514e-07 | 0.75101 | 20040.9877 | 0.61295 | 0.88673 | 0.016083 |  | 0.85073 | 1.5207e-07 | 0.85987 | 54499.4353 | 0.97201 | 0.97313 | 0.0043904 | 0.35467 | 9.8124e-07 | 0.49602 | 43826.9771 | 0.69934 | 0.94951 | 0.024757 |  | 0.04523
0.61002 | 7.8391e-07 | 0.59613 | 18373.5402 | 0.62236 | 0.88799 | 0.014087 |  | 0.478 | 6.4237e-08 | 0.020559 | 29188.5511 | 0.44577 | 0.90943 | 0.0013623 | 0.05719 | 4.6647e-07 | 0.064028 | 32391.0522 | 0.21994 | 0.89438 | 0.011073 |  | 0.026522
0.48861 | 6.2491e-07 | 0.84931 | 21519.0032 | 0.36634 | 0.85182 | 0.013839 |  | 0.40233 | 5.3655e-08 | 0.036361 | 30671.4033 | 0.57139 | 0.92261 | 0.0011229 | 0.82492 | 1.875e-06 | 0.76267 | 50664.6565 | 0.96403 | 0.98086 | 0.049732 |  | 0.064694
0.34575 | 4.6546e-07 | 0.8012 | 20726.7765 | 0.13965 | 0.80411 | 0.011866 |  | 0.59049 | 8.2368e-08 | 0.50381 | 43998.5763 | 0.77694 | 0.94359 | 0.0021169 | 0.16063 | 6.8367e-07 | 0.55136 | 45063.1681 | 0.77227 | 0.95656 | 0.017337 |  | 0.03132
0.37372 | 4.9525e-07 | 0.40504 | 16679.5087 | 0.18798 | 0.81743 | 0.011297 |  | 0.64585 | 9.2855e-08 | 0.38042 | 41320.9155 | 0.75923 | 0.94168 | 0.0022809 | 0.87829 | 2.075e-06 | 0.48602 | 43607.764 | 0.86805 | 0.96672 | 0.049787 |  | 0.063365
0.15021 | 2.6022e-07 | 0.60142 | 18423.9114 | 0.33218 | 0.84625 | 0.0055333 |  | 0.33492 | 4.4948e-08 | 0.6743 | 48067.613 | 0.32601 | 0.89505 | 0.0013801 | 0.60813 | 1.3761e-06 | 0.42129 | 42204.5533 | 0.76103 | 0.95545 | 0.033115 |  | 0.040029
0.22384 | 3.3864e-07 | 0.91067 | 22901.9808 | 0.75311 | 0.906 | 0.0063018 |  | 0.70908 | 1.0674e-07 | 0.58052 | 45736.2063 | 0.06531 | 0.83759 | 0.0035632 | 0.27962 | 8.7131e-07 | 0.26547 | 38742.3461 | 0.38957 | 0.91825 | 0.021738 |  | 0.031603
0.4269 | 5.5354e-07 | 0.37096 | 16385.2543 | 0.852 | 0.92161 | 0.0079807 |  | 0.53472 | 7.2941e-08 | 0.066851 | 32534.8765 | 0.39437 | 0.90356 | 0.0016883 | 0.35127 | 9.763e-07 | 0.60587 | 46337.8704 | 0.24052 | 0.89788 | 0.029043 |  | 0.038712
0.43445 | 5.6203e-07 | 0.026847 | 11898.1656 | 0.077521 | 0.78 | 0.013439 |  | 0.22024 | 3.1075e-08 | 0.18825 | 36795.3061 | 0.32268 | 0.89461 | 0.00079836 | 0.039491 | 4.1193e-07 | 0.35286 | 40720.1201 | 0.99165 | 0.98903 | 0.0086907 |  | 0.022928
0.54994 | 7.0143e-07 | 0.059899 | 12821.4551 | 0.2658 | 0.83433 | 0.013931 |  | 0.90386 | 1.8097e-07 | 0.38608 | 41443.5994 | 0.97975 | 0.97571 | 0.0040441 | 0.66911 | 1.49e-06 | 0.0059975 | 26570.0922 | 0.62937 | 0.94288 | 0.026119 |  | 0.044095
0.62183 | 8.0122e-07 | 0.18609 | 14640.1229 | 0.86339 | 0.92366 | 0.010776 |  | 0.50697 | 6.8586e-08 | 0.73232 | 49710.4007 | 0.5307 | 0.91846 | 0.0020556 | 0.11099 | 5.917e-07 | 0.053943 | 31838.9938 | 0.48216 | 0.92841 | 0.012456 |  | 0.025287
0.92989 | 1.6481e-06 | 0.13876 | 14084.3549 | 0.64315 | 0.89078 | 0.026107 |  | 0.83528 | 1.4551e-07 | 0.32441 | 40091.5757 | 0.13728 | 0.8619 | 0.0042742 | 0.96114 | 2.651e-06 | 0.91913 | 58096.0553 | 0.13943 | 0.87748 | 0.096022 |  | 0.1264
0.18473 | 2.9754e-07 | 0.44424 | 17016.8023 | 0.59256 | 0.884 | 0.0052614 |  | 0.5614 | 7.7329e-08 | 0.21581 | 37523.2072 | 0.91729 | 0.96151 | 0.0016557 | 0.12408 | 6.1737e-07 | 0.71608 | 49229.5719 | 0.60538 | 0.9406 | 0.017506 |  | 0.024423
0.63492 | 8.2093e-07 | 0.90851 | 22841.3528 | 0.75216 | 0.90586 | 0.015263 |  | 0.73501 | 1.1323e-07 | 0.6201 | 46683.5476 | 0.18659 | 0.87289 | 0.0035678 | 0.10136 | 5.7194e-07 | 0.41603 | 42091.039 | 0.8462 | 0.96424 | 0.013398 |  | 0.032228
0.18333 | 2.9605e-07 | 0.41493 | 16764.5981 | 0.89448 | 0.92971 | 0.0041301 |  | 0.27888 | 3.8066e-08 | 0.50071 | 43930.2285 | 0.51441 | 0.91678 | 0.0010441 | 0.8707 | 2.0425e-06 | 0.91418 | 57721.6619 | 0.61954 | 0.94195 | 0.065911 |  | 0.071086
0.16539 | 2.768e-07 | 0.18888 | 14670.4593 | 0.27141 | 0.83541 | 0.0056871 |  | 0.7782 | 1.2544e-07 | 0.08145 | 33220.5436 | 0.19351 | 0.87424 | 0.0032036 | 0.73795 | 1.6377e-06 | 0.56007 | 45262.2655 | 0.67136 | 0.94686 | 0.042718 |  | 0.051608
0.15455 | 2.6499e-07 | 0.43368 | 16925.8216 | 0.49549 | 0.87083 | 0.0049514 |  | 0.82631 | 1.4196e-07 | 0.84084 | 53615.081 | 0.12562 | 0.85884 | 0.0050238 | 0.60654 | 1.3733e-06 | 0.39695 | 41678.8414 | 0.25477 | 0.90017 | 0.037771 |  | 0.047746
0.93833 | 1.708e-06 | 0.95506 | 24568.3817 | 0.72227 | 0.90161 | 0.033638 |  | 0.39421 | 5.2575e-08 | 0.58756 | 45901.5881 | 0.97305 | 0.97345 | 0.0012969 | 0.60329 | 1.3676e-06 | 0.050462 | 31631.8975 | 0.43833 | 0.92376 | 0.029114 |  | 0.064049
0.89731 | 1.4674e-06 | 0.0090626 | 10909.5073 | 0.26486 | 0.83415 | 0.027996 |  | 0.80535 | 1.343e-07 | 0.19486 | 36974.0618 | 0.31668 | 0.8938 | 0.0034685 | 0.033792 | 3.9147e-07 | 0.82844 | 53082.752 | 0.95707 | 0.97945 | 0.010881 |  | 0.042346
0.30504 | 4.228e-07 | 0.15358 | 14267.8353 | 0.92858 | 0.93755 | 0.0051409 |  | 0.49728 | 6.7109e-08 | 0.5667 | 45414.8581 | 0.29024 | 0.89013 | 0.0020023 | 0.56324 | 1.2991e-06 | 0.98215 | 66842.0322 | 0.85549 | 0.96528 | 0.045863 |  | 0.053006
0.072013 | 1.6665e-07 | 0.24485 | 15242.5149 | 0.53201 | 0.87584 | 0.002925 |  | 0.44194 | 5.9068e-08 | 0.61172 | 46479.1358 | 0.21159 | 0.8776 | 0.0018381 | 0.57425 | 1.3176e-06 | 0.36011 | 40878.8301 | 0.028116 | 0.82597 | 0.042331 |  | 0.047094
0.48046 | 6.1519e-07 | 0.15567 | 14292.8525 | 0.85427 | 0.92201 | 0.0082565 |  | 0.18334 | 2.6721e-08 | 0.8588 | 54447.4418 | 0.11762 | 0.8566 | 0.00095878 | 0.8095 | 1.8268e-06 | 0.4476 | 42772.6577 | 0.65535 | 0.94535 | 0.045681 |  | 0.054896
0.22189 | 3.3661e-07 | 0.76824 | 20264.2912 | 0.94716 | 0.94275 | 0.0049034 |  | 0.42272 | 5.6409e-08 | 0.80821 | 52274.4944 | 0.4755 | 0.91266 | 0.0017772 | 0.01222 | 2.8511e-07 | 0.94596 | 60559.1057 | 0.1437 | 0.87856 | 0.010618 |  | 0.017298
0.1593 | 2.7018e-07 | 0.011625 | 11116.0105 | 0.89005 | 0.92879 | 0.0030801 |  | 0.62168 | 8.8115e-08 | 0.57662 | 45645.1442 | 0.21381 | 0.878 | 0.0027074 | 0.52625 | 1.239e-06 | 0.48761 | 43642.5889 | 0.14049 | 0.87775 | 0.036999 |  | 0.042786
0.97332 | 2.0909e-06 | 0.91394 | 22996.2306 | 0.24822 | 0.83085 | 0.050956 |  | 0.96613 | 2.4771e-07 | 0.084433 | 33350.5371 | 0.21806 | 0.87875 | 0.0062608 | 0.51278 | 1.2176e-06 | 0.97516 | 65025.431 | 0.99007 | 0.98831 | 0.040373 |  | 0.097589
0.75184 | 1.0285e-06 | 0.95713 | 24677.7337 | 0.14057 | 0.80439 | 0.02783 |  | 0.63488 | 9.0671e-08 | 0.45051 | 42835.709 | 0.00077432 | 0.72399 | 0.0035982 | 0.36163 | 9.9137e-07 | 0.55488 | 45143.4066 | 0.16479 | 0.88352 | 0.029886 |  | 0.061315
0.76161 | 1.0493e-06 | 0.2205 | 15001.4298 | 0.77944 | 0.90989 | 0.015445 |  | 0.35707 | 4.7749e-08 | 0.59498 | 46077.3054 | 0.54765 | 0.9202 | 0.0013461 | 0.62532 | 1.407e-06 | 0.90216 | 56885.1 | 0.86566 | 0.96644 | 0.042811 |  | 0.059602
0.15113 | 2.6123e-07 | 0.97872 | 26255.0903 | 0.12873 | 0.80061 | 0.0073084 |  | 0.44807 | 5.993e-08 | 0.34123 | 40464.4373 | 0.75162 | 0.94088 | 0.0014512 | 0.28185 | 8.7462e-07 | 0.36357 | 40954.4388 | 0.891 | 0.96949 | 0.019701 |  | 0.02846
0.19367 | 3.0702e-07 | 0.42461 | 16847.8709 | 0.13091 | 0.80133 | 0.0074158 |  | 0.59818 | 8.375e-08 | 0.77229 | 50984.6499 | 0.00073972 | 0.72299 | 0.0035759 | 0.5658 | 1.3034e-06 | 0.19489 | 36975.0686 | 0.73823 | 0.95323 | 0.02831 |  | 0.039301
0.92803 | 1.6359e-06 | 0.067097 | 12970.6722 | 0.88667 | 0.92811 | 0.020148 |  | 0.23692 | 3.305e-08 | 0.74791 | 50190.5754 | 0.56228 | 0.92169 | 0.00099116 | 0.16024 | 6.83e-07 | 0.55661 | 45182.9282 | 0.7117 | 0.95069 | 0.017619 |  | 0.038759
0.094742 | 1.9591e-07 | 0.85714 | 21666.2526 | 0.019793 | 0.73169 | 0.0061576 |  | 0.40791 | 5.4403e-08 | 0.26871 | 38818.6004 | 0.48965 | 0.91417 | 0.0013743 | 0.22566 | 7.8959e-07 | 0.86178 | 54593.4213 | 0.67746 | 0.94744 | 0.024056 |  | 0.031588
0.34945 | 4.6937e-07 | 0.29193 | 15684.8124 | 0.47355 | 0.86776 | 0.0086315 |  | 0.073987 | 1.3336e-08 | 0.29539 | 39437.0521 | 0.8678 | 0.95431 | 0.00030434 | 0.76713 | 1.7092e-06 | 0.8328 | 53266.0486 | 0.49656 | 0.9299 | 0.052827 |  | 0.061763
0.71115 | 9.4842e-07 | 0.311 | 15857.4948 | 0.85532 | 0.9222 | 0.013399 |  | 0.39085 | 5.2131e-08 | 0.29195 | 39358.1876 | 0.029745 | 0.81428 | 0.0016835 | 0.81038 | 1.8295e-06 | 0.029886 | 30136.919 | 0.27161 | 0.90276 | 0.040471 |  | 0.055553
0.77453 | 1.0781e-06 | 0.2261 | 15057.7381 | 0.80596 | 0.91396 | 0.015544 |  | 0.15466 | 2.3323e-08 | 0.11832 | 34658.9228 | 0.87914 | 0.95583 | 0.00047656 | 0.37665 | 1.0133e-06 | 0.27891 | 39057.2513 | 0.37912 | 0.91702 | 0.025511 |  | 0.041532
0.36324 | 4.8403e-07 | 0.81725 | 20972.9145 | 0.11854 | 0.79713 | 0.012648 |  | 0.15777 | 2.3694e-08 | 0.68019 | 48225.6954 | 0.87373 | 0.9551 | 0.00063887 | 0.62049 | 1.3982e-06 | 0.67342 | 48044.2324 | 0.60807 | 0.94086 | 0.038845 |  | 0.052132
0.98631 | 2.388e-06 | 0.56048 | 18041.6622 | 0.7748 | 0.90919 | 0.038582 |  | 0.69396 | 1.0319e-07 | 0.74339 | 50049.556 | 0.69495 | 0.93503 | 0.0030019 | 0.031539 | 3.8284e-07 | 0.68634 | 48392.3906 | 0.21754 | 0.89396 | 0.011837 |  | 0.053421
0.51014 | 6.5104e-07 | 0.082778 | 13262.22 | 0.24238 | 0.82966 | 0.013296 |  | 0.71698 | 1.0866e-07 | 0.2442 | 38232.0892 | 0.098662 | 0.85075 | 0.0031878 | 0.24288 | 8.1609e-07 | 0.98196 | 66783.0819 | 0.89005 | 0.96938 | 0.028605 |  | 0.045089
0.46213 | 5.937e-07 | 0.98938 | 27742.9358 | 0.98631 | 0.96003 | 0.0099852 |  | 0.79963 | 1.3234e-07 | 0.13084 | 35084.5902 | 0.41371 | 0.90581 | 0.0031948 | 0.77875 | 1.7397e-06 | 0.93292 | 59253.4545 | 0.063551 | 0.85103 | 0.066566 |  | 0.079746
0.76722 | 1.0617e-06 | 0.88613 | 22275.3395 | 0.40905 | 0.85841 | 0.023319 |  | 0.12776 | 2.0094e-08 | 0.53447 | 44681.0171 | 0.57549 | 0.92303 | 0.00054985 | 0.39164 | 1.0352e-06 | 0.041109 | 31020.6462 | 0.33771 | 0.91191 | 0.022629 |  | 0.046498
0.94988 | 1.804e-06 | 0.031837 | 12077.6141 | 0.17318 | 0.81366 | 0.038312 |  | 0.027605 | 6.5994e-09 | 0.91853 | 58049.6953 | 0.4809 | 0.91324 | 0.00022508 | 0.76587 | 1.706e-06 | 0.21372 | 37469.6561 | 0.47925 | 0.92811 | 0.040407 |  | 0.078944
0.40157 | 5.2547e-07 | 0.42482 | 16849.6653 | 0.58325 | 0.88275 | 0.0093049 |  | 0.36515 | 4.8784e-08 | 0.36939 | 41081.2198 | 0.69407 | 0.93494 | 0.0012149 | 0.28061 | 8.7278e-07 | 0.87128 | 55077.5042 | 0.84931 | 0.96459 | 0.025892 |  | 0.036411
0.93836 | 1.7082e-06 | 0.41521 | 16767.0121 | 0.75664 | 0.90651 | 0.026971 |  | 0.52235 | 7.0976e-08 | 0.31971 | 39986.542 | 0.27736 | 0.88826 | 0.0019552 | 0.015061 | 3.0375e-07 | 0.025432 | 29716.9662 | 0.54407 | 0.93467 | 0.0059568 |  | 0.034883
0.0042329 | 3.6133e-08 | 0.19832 | 14771.7511 | 0.90898 | 0.93284 | 0.00046152 |  | 0.095377 | 1.6096e-08 | 0.86776 | 54894.5604 | 0.62909 | 0.92841 | 0.0005111 | 0.13997 | 6.4704e-07 | 0.4259 | 42304.0299 | 0.30865 | 0.90806 | 0.017639 |  | 0.018612
0.96432 | 1.9595e-06 | 0.024758 | 11815.5925 | 0.74878 | 0.90538 | 0.026723 |  | 0.89105 | 1.7281e-07 | 0.90726 | 57228.577 | 0.67459 | 0.93297 | 0.0056282 | 0.36018 | 9.8927e-07 | 0.37311 | 41162.2298 | 0.11905 | 0.87193 | 0.028851 |  | 0.061202
0.54545 | 6.956e-07 | 0.16118 | 14358.1991 | 0.55646 | 0.87915 | 0.011754 |  | 0.44481 | 5.947e-08 | 0.30441 | 39642.0443 | 0.19499 | 0.87452 | 0.0016845 | 0.15531 | 6.7443e-07 | 0.45949 | 43030.2428 | 0.44021 | 0.92396 | 0.0179 |  | 0.031338
0.80074 | 1.1413e-06 | 0.96149 | 24925.5207 | 0.0085457 | 0.70547 | 0.03948 |  | 0.42713 | 5.7014e-08 | 0.0012466 | 23984.5796 | 0.46236 | 0.91124 | 0.0010663 | 0.56144 | 1.2962e-06 | 0.84066 | 53606.7954 | 0.94493 | 0.97725 | 0.036534 |  | 0.07708
0.73007 | 9.8434e-07 | 0.654 | 18943.7781 | 0.10987 | 0.79397 | 0.025169 |  | 0.1027 | 1.7015e-08 | 0.84896 | 53981.3403 | 0.13722 | 0.86189 | 0.00060167 | 0.65771 | 1.4677e-06 | 0.59035 | 45967.5025 | 0.2357 | 0.89708 | 0.043494 |  | 0.069264
0.1421 | 2.5123e-07 | 0.91914 | 23152.6648 | 0.41827 | 0.85978 | 0.0055864 |  | 0.87566 | 1.6414e-07 | 0.22318 | 37710.8033 | 0.84584 | 0.95151 | 0.0036421 | 0.46153 | 1.1388e-06 | 0.38905 | 41508.0539 | 0.45943 | 0.92603 | 0.029265 |  | 0.038493
0.84897 | 1.2799e-06 | 0.61758 | 18579.6791 | 0.36628 | 0.85181 | 0.026743 |  | 0.36616 | 4.8914e-08 | 0.94773 | 60757.6443 | 0.073556 | 0.8413 | 0.0019301 | 0.85624 | 1.9848e-06 | 0.98203 | 66805.3667 | 0.37763 | 0.91684 | 0.075241 |  | 0.10391
0.73473 | 9.9352e-07 | 0.82399 | 21081.1179 | 0.12788 | 0.80033 | 0.025759 |  | 0.36746 | 4.9081e-08 | 0.59253 | 46019.0377 | 0.16246 | 0.86784 | 0.0015483 | 0.92451 | 2.3238e-06 | 0.80044 | 51981.2939 | 0.44346 | 0.92431 | 0.071232 |  | 0.09854
0.3752 | 4.9684e-07 | 0.92568 | 23362.1859 | 0.94914 | 0.94337 | 0.0079398 |  | 0.59983 | 8.4048e-08 | 0.37738 | 41254.844 | 0.98012 | 0.97585 | 0.0018697 | 0.69792 | 1.5488e-06 | 0.035136 | 30575.9272 | 0.65329 | 0.94515 | 0.029822 |  | 0.039631
0.23455 | 3.4977e-07 | 0.41153 | 16735.2991 | 0.69345 | 0.89761 | 0.0057643 |  | 0.69889 | 1.0433e-07 | 0.6111 | 46464.3221 | 0.41904 | 0.90643 | 0.0030523 | 0.45608 | 1.1306e-06 | 0.26387 | 38704.4496 | 0.82895 | 0.96237 | 0.024783 |  | 0.033599
0.67678 | 8.879e-07 | 0.30043 | 15762.1339 | 0.12479 | 0.79929 | 0.021204 |  | 0.31994 | 4.3081e-08 | 0.72405 | 49463.1424 | 0.84464 | 0.95136 | 0.0011972 | 0.016587 | 3.1285e-07 | 0.016994 | 28737.5027 | 0.4375 | 0.92366 | 0.0062441 |  | 0.028646
0.32409 | 4.4267e-07 | 0.036108 | 12215.3657 | 0.45271 | 0.8648 | 0.0075809 |  | 0.72143 | 1.0976e-07 | 0.87709 | 55387.7833 | 0.18928 | 0.87342 | 0.0038721 | 0.21218 | 7.685e-07 | 0.90141 | 56835.8767 | 0.45543 | 0.9256 | 0.025223 |  | 0.036676
0.9493 | 1.7987e-06 | 0.049533 | 12583.2245 | 0.58271 | 0.88268 | 0.028475 |  | 0.2109 | 2.9972e-08 | 0.5123 | 44186.2673 | 0.58031 | 0.92351 | 0.00081235 | 0.3536 | 9.7968e-07 | 0.092897 | 33704.1206 | 0.78249 | 0.95758 | 0.01945 |  | 0.048737
0.65017 | 8.4458e-07 | 0.85125 | 21555.0096 | 0.04881 | 0.76265 | 0.024503 |  | 0.62529 | 8.8806e-08 | 0.074257 | 32893.8175 | 0.49589 | 0.91483 | 0.0019987 | 0.89389 | 2.1479e-06 | 0.063285 | 32352.4889 | 0.13003 | 0.87502 | 0.053918 |  | 0.08042
0.76992 | 1.0677e-06 | 0.15206 | 14249.4672 | 0.87918 | 0.92663 | 0.013911 |  | 0.51566 | 6.9929e-08 | 0.5045 | 44013.6397 | 0.20323 | 0.87607 | 0.0021073 | 0.02047 | 3.3386e-07 | 0.87964 | 55527.5611 | 0.30585 | 0.90767 | 0.011113 |  | 0.027132
0.31312 | 4.3121e-07 | 0.54389 | 17890.872 | 0.79462 | 0.91219 | 0.0068355 |  | 0.26744 | 3.6689e-08 | 0.043353 | 31175.671 | 0.37196 | 0.90088 | 0.00083379 | 0.43522 | 1.0994e-06 | 0.56101 | 45283.9603 | 0.37611 | 0.91666 | 0.030843 |  | 0.038513
0.92552 | 1.6198e-06 | 0.75063 | 20036.1477 | 0.39501 | 0.85628 | 0.034287 |  | 0.49008 | 6.6027e-08 | 0.057379 | 32034.4456 | 0.62231 | 0.92773 | 0.0013991 | 0.031383 | 3.8223e-07 | 0.43646 | 42531.9752 | 0.99657 | 0.99206 | 0.0083298 |  | 0.044016
0.60549 | 7.7738e-07 | 0.59156 | 18330.3345 | 0.7088 | 0.89973 | 0.013239 |  | 0.6757 | 9.9112e-08 | 0.28387 | 39172.1306 | 0.82209 | 0.94866 | 0.0022873 | 0.44166 | 1.109e-06 | 0.59841 | 46158.9414 | 0.17069 | 0.88481 | 0.033836 |  | 0.049362
0.916 | 1.563e-06 | 0.13687 | 14060.1883 | 0.42169 | 0.86029 | 0.028583 |  | 0.17568 | 2.5816e-08 | 0.15991 | 35991.4397 | 0.49731 | 0.91498 | 0.00061733 | 0.43012 | 1.0918e-06 | 0.46859 | 43227.6714 | 0.35583 | 0.91419 | 0.02978 |  | 0.05898
0.31893 | 4.3728e-07 | 0.66363 | 19043.4688 | 0.95177 | 0.94421 | 0.0060685 |  | 0.49068 | 6.6117e-08 | 0.7409 | 49972.4346 | 0.70087 | 0.93563 | 0.0019185 | 0.52524 | 1.2374e-06 | 0.77684 | 51139.6013 | 0.349 | 0.91334 | 0.038291 |  | 0.046278
0.30848 | 4.2638e-07 | 0.64791 | 18881.5108 | 0.74488 | 0.90482 | 0.0071974 |  | 0.074019 | 1.3341e-08 | 0.18899 | 36815.416 | 0.50992 | 0.91631 | 0.00032282 | 0.82694 | 1.8815e-06 | 0.47182 | 43297.8872 | 0.17718 | 0.88619 | 0.054856 |  | 0.062377
0.47473 | 6.0842e-07 | 0.85927 | 21707.4982 | 0.34302 | 0.84805 | 0.013699 |  | 0.41646 | 5.5557e-08 | 0.90245 | 56904.5212 | 0.74344 | 0.94002 | 0.0017778 | 0.96661 | 2.7233e-06 | 0.89 | 56123.431 | 0.1258 | 0.87385 | 0.096876 |  | 0.11235
0.24771 | 3.6341e-07 | 0.018895 | 11551.527 | 0.67566 | 0.89517 | 0.0052161 |  | 0.97848 | 2.7618e-07 | 0.73008 | 49643.0551 | 0.9279 | 0.96332 | 0.0074912 | 0.63206 | 1.4193e-06 | 0.24524 | 38257.3162 | 0.44792 | 0.9248 | 0.034458 |  | 0.047166
0.9338 | 1.675e-06 | 0.59688 | 18380.6706 | 0.15813 | 0.80957 | 0.040403 |  | 0.25628 | 3.5353e-08 | 0.92223 | 58340.1994 | 0.72511 | 0.93811 | 0.0011591 | 0.15237 | 6.6926e-07 | 0.034543 | 30528.8911 | 0.50828 | 0.93109 | 0.013552 |  | 0.055114
0.62962 | 8.1288e-07 | 0.29128 | 15678.9043 | 0.3514 | 0.84942 | 0.016135 |  | 0.51329 | 6.9561e-08 | 0.79429 | 51755.1509 | 0.071527 | 0.84042 | 0.0024852 | 0.59607 | 1.3549e-06 | 0.15139 | 35735.6278 | 0.48746 | 0.92896 | 0.030921 |  | 0.049542
0.11397 | 2.1907e-07 | 0.13343 | 14015.7246 | 0.30159 | 0.84096 | 0.0043431 |  | 0.035784 | 7.9175e-09 | 0.93532 | 59476.217 | 0.35292 | 0.89852 | 0.00028194 | 0.64301 | 1.4397e-06 | 0.083541 | 33311.9542 | 0.033598 | 0.83127 | 0.041213 |  | 0.045838
0.14827 | 2.5808e-07 | 0.12099 | 13849.3484 | 0.40679 | 0.85807 | 0.0047422 |  | 0.8533 | 1.5322e-07 | 0.57701 | 45654.0748 | 0.48365 | 0.91354 | 0.0043556 | 0.29856 | 8.9928e-07 | 0.26702 | 38778.942 | 0.35294 | 0.91383 | 0.022722 |  | 0.03182
0.76424 | 1.0551e-06 | 0.9726 | 25696.197 | 0.65972 | 0.89301 | 0.021994 |  | 0.71416 | 1.0797e-07 | 0.16412 | 36115.2396 | 0.98764 | 0.97908 | 0.0021068 | 0.75662 | 1.6827e-06 | 0.96266 | 62723.4737 | 0.90159 | 0.97085 | 0.055531 |  | 0.079632
0.7619 | 1.05e-06 | 0.22961 | 15092.8399 | 0.96646 | 0.94951 | 0.012167 |  | 0.35257 | 4.7175e-08 | 0.41738 | 42120.0362 | 0.55751 | 0.92121 | 0.0012408 | 0.2105 | 7.6584e-07 | 0.3993 | 41729.7098 | 0.43343 | 0.92322 | 0.019903 |  | 0.033311
0.093708 | 1.9463e-07 | 0.60312 | 18440.2067 | 0.60335 | 0.88545 | 0.003542 |  | 0.36901 | 4.9281e-08 | 0.73349 | 49745.724 | 0.56426 | 0.92189 | 0.0014672 | 0.8958 | 2.1574e-06 | 0.74199 | 50005.9297 | 0.046619 | 0.84127 | 0.075379 |  | 0.080388
0.42393 | 5.5022e-07 | 0.7105 | 19554.7147 | 0.27824 | 0.8367 | 0.012372 |  | 0.38308 | 5.111e-08 | 0.57739 | 45662.9244 | 0.69849 | 0.93538 | 0.0013808 | 0.89527 | 2.1548e-06 | 0.65726 | 47619.5821 | 0.036126 | 0.83346 | 0.074196 |  | 0.087949
0.46176 | 5.9327e-07 | 0.67496 | 19162.8969 | 0.48081 | 0.86878 | 0.011758 |  | 0.9611 | 2.3896e-07 | 0.12014 | 34722.5287 | 0.5882 | 0.92431 | 0.0054191 | 0.8247 | 1.8743e-06 | 0.17467 | 36418.1346 | 0.93381 | 0.97543 | 0.037324 |  | 0.054501
0.38669 | 5.0926e-07 | 0.10643 | 13641.2337 | 0.83859 | 0.91929 | 0.0067938 |  | 0.64979 | 9.3653e-08 | 0.42311 | 42243.6474 | 0.064814 | 0.83735 | 0.0029908 | 0.94747 | 2.5047e-06 | 0.19215 | 36901.3161 | 0.3975 | 0.91917 | 0.060213 |  | 0.069998
0.44919 | 5.7879e-07 | 0.35268 | 16226.2172 | 0.0686 | 0.7753 | 0.015033 |  | 0.52432 | 7.1286e-08 | 0.22662 | 37797.4191 | 0.98542 | 0.97802 | 0.0014549 | 0.97116 | 2.7926e-06 | 0.356 | 40788.9686 | 0.22657 | 0.89554 | 0.076559 |  | 0.093047
0.33673 | 4.5595e-07 | 0.29377 | 15701.6112 | 0.12756 | 0.80022 | 0.010844 |  | 0.5566 | 7.6523e-08 | 0.18654 | 36748.6196 | 0.021631 | 0.80538 | 0.002437 | 0.87413 | 2.057e-06 | 0.21657 | 37542.7112 | 0.59464 | 0.93957 | 0.047167 |  | 0.060448
0.43472 | 5.6233e-07 | 0.4113 | 16733.3377 | 0.798 | 0.91272 | 0.0085937 |  | 0.15431 | 2.3282e-08 | 0.60715 | 46368.6433 | 0.53179 | 0.91858 | 0.00066189 | 0.81864 | 1.855e-06 | 0.98609 | 68183.6477 | 0.63171 | 0.94311 | 0.068886 |  | 0.078142
0.3133 | 4.3141e-07 | 0.058076 | 12781.7579 | 0.14378 | 0.80538 | 0.0095756 |  | 0.5518 | 7.5726e-08 | 0.1109 | 34394.2491 | 0.40882 | 0.90525 | 0.0018074 | 0.94702 | 2.5006e-06 | 0.13597 | 35252.0877 | 0.1189 | 0.87189 | 0.066491 |  | 0.077874
0.063117 | 1.5442e-07 | 0.16682 | 14423.8124 | 0.45171 | 0.86466 | 0.0027937 |  | 0.32011 | 4.3103e-08 | 0.8164 | 52593.3795 | 0.16078 | 0.86747 | 0.0014837 | 0.67563 | 1.503e-06 | 0.41071 | 41976.1963 | 0.31671 | 0.90915 | 0.040641 |  | 0.044918
0.35079 | 4.7079e-07 | 0.69934 | 19428.555 | 0.4988 | 0.87129 | 0.009293 |  | 0.13305 | 2.0734e-08 | 0.87434 | 55239.181 | 0.29091 | 0.89023 | 0.00070919 | 0.7771 | 1.7353e-06 | 0.044165 | 31230.3127 | 0.44453 | 0.92443 | 0.036536 |  | 0.046539
0.91573 | 1.5615e-06 | 0.88204 | 22182.3189 | 0.70813 | 0.89963 | 0.02931 |  | 0.83896 | 1.4702e-07 | 0.63659 | 47092.656 | 0.87321 | 0.95503 | 0.0038852 | 0.98793 | 3.1923e-06 | 0.18426 | 36685.9749 | 0.88723 | 0.96902 | 0.065405 |  | 0.0986
0.74974 | 1.024e-06 | 0.023355 | 11757.1185 | 0.41077 | 0.85866 | 0.017848 |  | 0.13159 | 2.0558e-08 | 0.62742 | 46864.0668 | 0.31783 | 0.89396 | 0.00062161 | 0.23356 | 8.0181e-07 | 0.8656 | 54784.5889 | 0.28372 | 0.90455 | 0.026572 |  | 0.045041
0.41812 | 5.4374e-07 | 0.31597 | 15901.9777 | 0.10477 | 0.79201 | 0.013331 |  | 0.80544 | 1.3433e-07 | 0.042404 | 31110.8135 | 0.96991 | 0.97251 | 0.0023555 | 0.75271 | 1.6731e-06 | 0.0062407 | 26644.9032 | 0.21347 | 0.89323 | 0.035559 |  | 0.051245
0.68262 | 8.978e-07 | 0.81323 | 20909.7419 | 0.14187 | 0.80479 | 0.022907 |  | 0.4616 | 6.1855e-08 | 0.66683 | 47869.5199 | 0.7988 | 0.946 | 0.0016932 | 0.72248 | 1.6023e-06 | 0.3372 | 40375.4839 | 0.8608 | 0.96588 | 0.036031 |  | 0.060631
0.225 | 3.3985e-07 | 0.39797 | 16618.6351 | 0.85801 | 0.92268 | 0.0049074 |  | 0.96025 | 2.3758e-07 | 0.30988 | 39765.7259 | 0.14103 | 0.86284 | 0.0069304 | 0.49323 | 1.1872e-06 | 0.37261 | 41151.2176 | 0.80433 | 0.95979 | 0.027626 |  | 0.039464
0.044754 | 1.2704e-07 | 0.173 | 14494.4677 | 0.71278 | 0.90028 | 0.0019387 |  | 0.47517 | 6.3822e-08 | 0.7588 | 50538.4436 | 0.00867 | 0.78114 | 0.0024834 | 0.81729 | 1.8507e-06 | 0.97226 | 64410.1554 | 0.72128 | 0.9516 | 0.064565 |  | 0.068987
0.29402 | 4.1135e-07 | 0.91813 | 23121.4737 | 0.1529 | 0.80808 | 0.010759 |  | 0.55937 | 7.6988e-08 | 0.22351 | 37719.0008 | 0.027082 | 0.81163 | 0.0024488 | 0.70432 | 1.5624e-06 | 0.39667 | 41672.8238 | 0.66342 | 0.94611 | 0.038177 |  | 0.051385
0.37971 | 5.0171e-07 | 0.85569 | 21638.5275 | 0.84495 | 0.92038 | 0.0084953 |  | 0.65506 | 9.4735e-08 | 0.36277 | 40936.8588 | 0.39114 | 0.90318 | 0.0025548 | 0.15827 | 6.7959e-07 | 0.81162 | 52405.8706 | 0.90364 | 0.97112 | 0.019012 |  | 0.030062
0.65671 | 8.5498e-07 | 0.71831 | 19644.8073 | 0.67456 | 0.89502 | 0.015379 |  | 0.43905 | 5.8664e-08 | 0.76487 | 50737.1789 | 0.17413 | 0.87035 | 0.0019615 | 0.14295 | 6.5246e-07 | 0.48399 | 43563.3865 | 0.27012 | 0.90254 | 0.018397 |  | 0.035737
0.50744 | 6.4772e-07 | 0.73039 | 19787.3294 | 0.01956 | 0.73131 | 0.019932 |  | 0.9344 | 2.0566e-07 | 0.61572 | 46576.458 | 0.55058 | 0.9205 | 0.0058409 | 0.56327 | 1.2992e-06 | 0.32549 | 40115.5919 | 0.25108 | 0.89959 | 0.03487 |  | 0.060643
0.2194 | 3.3402e-07 | 0.1163 | 13784.0136 | 0.11433 | 0.79562 | 0.0078118 |  | 0.72623 | 1.1097e-07 | 0.39792 | 41699.7965 | 0.49133 | 0.91435 | 0.0029481 | 0.78109 | 1.7459e-06 | 0.8686 | 54938.1944 | 0.91333 | 0.97243 | 0.050854 |  | 0.061614
0.79637 | 1.1302e-06 | 0.19234 | 14707.8573 | 0.28832 | 0.83857 | 0.022953 |  | 0.68875 | 1.0201e-07 | 0.8228 | 52850.0818 | 0.95234 | 0.96811 | 0.0028946 | 0.10358 | 5.7656e-07 | 0.88441 | 55796.6116 | 0.33523 | 0.91159 | 0.019128 |  | 0.044976
0.68937 | 9.0944e-07 | 0.746 | 19978.1243 | 0.89163 | 0.92912 | 0.014087 |  | 0.307 | 4.1486e-08 | 0.70882 | 49020.192 | 0.89784 | 0.95849 | 0.0011255 | 0.45687 | 1.1317e-06 | 0.091085 | 33630.1791 | 0.45473 | 0.92553 | 0.024997 |  | 0.04021
0.24844 | 3.6416e-07 | 0.70777 | 19523.5442 | 0.23085 | 0.82725 | 0.0084517 |  | 0.75461 | 1.1853e-07 | 0.38525 | 41425.718 | 0.18948 | 0.87346 | 0.0034583 | 0.59741 | 1.3573e-06 | 0.89403 | 56367.5436 | 0.55189 | 0.93543 | 0.04346 |  | 0.05537
0.54078 | 6.8957e-07 | 0.22387 | 15035.4245 | 0.1582 | 0.80959 | 0.015699 |  | 0.082012 | 1.4387e-08 | 0.1978 | 37052.7064 | 0.044608 | 0.82603 | 0.00043941 | 0.75553 | 1.68e-06 | 0.1316 | 35109.6684 | 0.99459 | 0.99064 | 0.030594 |  | 0.046732
0.013591 | 6.6468e-08 | 0.49967 | 17497.8402 | 0.55802 | 0.87936 | 0.0012138 |  | 0.27717 | 3.7859e-08 | 0.35384 | 40741.5479 | 0.046715 | 0.8274 | 0.0012105 | 0.11323 | 5.9618e-07 | 0.05387 | 31834.7144 | 0.30858 | 0.90805 | 0.013419 |  | 0.015844
0.28926 | 4.0642e-07 | 0.38063 | 16469.0281 | 0.98027 | 0.95612 | 0.004762 |  | 0.25063 | 3.468e-08 | 0.19133 | 36879.0241 | 0.97571 | 0.9743 | 0.00070112 | 0.97052 | 2.7823e-06 | 0.21935 | 37613.6431 | 0.034804 | 0.83233 | 0.084417 |  | 0.08988
0.23416 | 3.4937e-07 | 0.13257 | 14004.5271 | 0.75033 | 0.9056 | 0.0051045 |  | 0.44736 | 5.9829e-08 | 0.50596 | 44045.9245 | 0.8435 | 0.95122 | 0.001509 | 0.28125 | 8.7372e-07 | 0.012945 | 28125.4735 | 0.94443 | 0.97716 | 0.013754 |  | 0.020368
0.88467 | 1.4115e-06 | 0.13998 | 14099.8403 | 0.79292 | 0.91193 | 0.019964 |  | 0.50516 | 6.8308e-08 | 0.96098 | 62469.538 | 0.7896 | 0.94497 | 0.0023454 | 0.44 | 1.1065e-06 | 0.86433 | 54720.6587 | 0.34948 | 0.9134 | 0.036046 |  | 0.058356
0.48669 | 6.2261e-07 | 0.68596 | 19281.2093 | 0.27265 | 0.83564 | 0.01398 |  | 0.3923 | 5.2322e-08 | 0.62445 | 46790.5771 | 0.084941 | 0.84588 | 0.0017418 | 0.65219 | 1.4571e-06 | 0.57205 | 45538.7012 | 0.59673 | 0.93977 | 0.038867 |  | 0.054589
0.54617 | 6.9653e-07 | 0.11319 | 13739.8468 | 0.79554 | 0.91234 | 0.0097144 |  | 0.19184 | 2.7723e-08 | 0.8221 | 52822.0121 | 0.91521 | 0.96117 | 0.00079807 | 0.74242 | 1.6483e-06 | 0.021394 | 29285.4557 | 0.45818 | 0.92589 | 0.033047 |  | 0.043559
0.62126 | 8.0038e-07 | 0.98995 | 27859.0464 | 0.17784 | 0.81488 | 0.022065 |  | 0.51039 | 6.9112e-08 | 0.070856 | 32732.0711 | 0.63456 | 0.92895 | 0.0014809 | 0.097254 | 5.6324e-07 | 0.71284 | 49135.6887 | 0.50871 | 0.93114 | 0.016282 |  | 0.039828
0.12627 | 2.3334e-07 | 0.7449 | 19964.387 | 0.88416 | 0.92761 | 0.0036403 |  | 0.32461 | 4.3661e-08 | 0.2725 | 38907.6635 | 0.51267 | 0.91659 | 0.0010975 | 0.30244 | 9.0499e-07 | 0.28932 | 39297.8611 | 0.91209 | 0.97226 | 0.019488 |  | 0.024226
0.87232 | 1.3622e-06 | 0.79712 | 20666.5837 | 0.86663 | 0.92425 | 0.022049 |  | 0.683 | 1.0072e-07 | 0.47332 | 43330.6778 | 0.25075 | 0.8842 | 0.0029511 | 0.62786 | 1.4116e-06 | 0.0080353 | 27133.8752 | 0.72376 | 0.95184 | 0.024184 |  | 0.049184
0.56531 | 7.2173e-07 | 0.33038 | 16030.1949 | 0.8333 | 0.9184 | 0.010472 |  | 0.51292 | 6.9503e-08 | 0.0521 | 31730.5244 | 0.50388 | 0.91567 | 0.0015231 | 0.25428 | 8.3338e-07 | 0.12291 | 34818.075 | 0.64923 | 0.94477 | 0.017739 |  | 0.029734
0.32027 | 4.3868e-07 | 0.16826 | 14440.4781 | 0.63695 | 0.88995 | 0.0070479 |  | 0.1569 | 2.3589e-08 | 0.6613 | 47724.722 | 0.25331 | 0.8846 | 0.0007364 | 0.94626 | 2.4935e-06 | 0.20267 | 37181.9397 | 0.65036 | 0.94487 | 0.055844 |  | 0.063628
0.90445 | 1.5018e-06 | 0.58919 | 18308.0029 | 0.087952 | 0.78496 | 0.039083 |  | 0.88386 | 1.6862e-07 | 0.43026 | 42397.9956 | 0.39015 | 0.90307 | 0.00466 | 0.84175 | 1.9317e-06 | 0.60896 | 46412.4101 | 0.1925 | 0.88929 | 0.058598 |  | 0.10234
0.46808 | 6.0063e-07 | 0.64146 | 18816.1993 | 0.34867 | 0.84898 | 0.012743 |  | 0.66338 | 9.647e-08 | 0.46995 | 43257.2407 | 0.32363 | 0.89473 | 0.0027565 | 0.98441 | 3.0768e-06 | 0.2049 | 37240.3677 | 0.54884 | 0.93513 | 0.071058 |  | 0.086557
0.54688 | 6.9745e-07 | 0.78191 | 20449.8198 | 0.0206 | 0.73299 | 0.02154 |  | 0.94898 | 2.2174e-07 | 0.74396 | 50067.2305 | 0.76145 | 0.94192 | 0.0063567 | 0.38789 | 1.0297e-06 | 0.10805 | 34289.9485 | 0.077699 | 0.85754 | 0.027988 |  | 0.055886
0.20336 | 3.1723e-07 | 0.54181 | 17872.1662 | 0.048414 | 0.76235 | 0.0087651 |  | 0.49717 | 6.7094e-08 | 0.56591 | 45396.6836 | 0.30045 | 0.89158 | 0.001995 | 0.23598 | 8.0554e-07 | 0.60313 | 46271.8543 | 0.18068 | 0.88692 | 0.024509 |  | 0.035269
0.10194 | 2.0472e-07 | 0.1091 | 13680.6396 | 0.18215 | 0.81598 | 0.0044428 |  | 0.089526 | 1.5353e-08 | 0.22109 | 37657.897 | 0.097021 | 0.8502 | 0.00044725 | 0.95867 | 2.6213e-06 | 0.46809 | 43216.8539 | 0.93173 | 0.97511 | 0.060948 |  | 0.065838
0.90097 | 1.4848e-06 | 0.46156 | 17166.2222 | 0.72918 | 0.90258 | 0.024174 |  | 0.19635 | 2.8255e-08 | 0.68798 | 48437.4667 | 0.029722 | 0.81426 | 0.0010169 | 0.33789 | 9.568e-07 | 0.52661 | 44504.7 | 0.6927 | 0.94888 | 0.024487 |  | 0.049678
0.81011 | 1.1656e-06 | 0.045353 | 12477.2596 | 0.48001 | 0.86867 | 0.019727 |  | 0.67162 | 9.8226e-08 | 0.27701 | 39012.9729 | 0.2097 | 0.87726 | 0.002737 | 0.6019 | 1.3651e-06 | 0.23023 | 37887.6569 | 0.92337 | 0.97386 | 0.028311 |  | 0.050774
0.40694 | 5.3137e-07 | 0.19146 | 14698.3664 | 0.57465 | 0.8816 | 0.0089541 |  | 0.3853 | 5.14e-08 | 0.86467 | 54737.7577 | 0.84701 | 0.95166 | 0.0015564 | 0.14872 | 6.6279e-07 | 0.70911 | 49028.4783 | 0.30352 | 0.90735 | 0.020122 |  | 0.030632
0.72871 | 9.8171e-07 | 0.51376 | 17621.899 | 0.30404 | 0.8414 | 0.020917 |  | 0.68287 | 1.0069e-07 | 0.44967 | 42817.5559 | 0.80485 | 0.94668 | 0.002511 | 0.45676 | 1.1316e-06 | 0.33877 | 40410.1141 | 0.83329 | 0.96284 | 0.025698 |  | 0.049126
0.19861 | 3.1223e-07 | 0.2333 | 15129.3845 | 0.64919 | 0.89159 | 0.0050709 |  | 0.0080383 | 2.8243e-09 | 0.88004 | 55549.7118 | 0.19236 | 0.87401 | 9.973e-05 | 0.91662 | 2.2731e-06 | 0.95676 | 61874.1413 | 0.93259 | 0.97524 | 0.073511 |  | 0.078682
0.49673 | 6.3468e-07 | 0.75538 | 20096.6061 | 0.81075 | 0.91472 | 0.010575 |  | 0.76492 | 1.2147e-07 | 0.461 | 43062.9808 | 0.63711 | 0.92921 | 0.0031836 | 0.63252 | 1.4202e-06 | 0.60286 | 46265.3761 | 0.24513 | 0.89863 | 0.042133 |  | 0.055892
0.060889 | 1.5126e-07 | 0.024975 | 11824.4277 | 0.56756 | 0.88065 | 0.0023691 |  | 0.0026049 | 1.3185e-09 | 0.3033 | 39616.9682 | 0.96963 | 0.97243 | 2.8583e-05 | 0.062253 | 4.8031e-07 | 0.54095 | 44827.0818 | 0.36684 | 0.91554 | 0.01341 |  | 0.015807
0.29579 | 4.1319e-07 | 0.45831 | 17138.1135 | 0.85507 | 0.92215 | 0.0060827 |  | 0.88427 | 1.6886e-07 | 0.86218 | 54613.1753 | 0.64972 | 0.93047 | 0.0053187 | 0.60258 | 1.3663e-06 | 0.052001 | 31724.6344 | 0.69483 | 0.94908 | 0.026664 |  | 0.038065
0.16711 | 2.7866e-07 | 0.67645 | 19178.7659 | 0.32598 | 0.8452 | 0.0060372 |  | 0.82755 | 1.4244e-07 | 0.12386 | 34850.4098 | 0.4661 | 0.91165 | 0.0033652 | 0.1395 | 6.4618e-07 | 0.38047 | 41321.9354 | 0.052941 | 0.84523 | 0.020045 |  | 0.029448
0.0094786 | 5.496e-08 | 0.68792 | 19302.502 | 0.61291 | 0.88673 | 0.0010157 |  | 0.14722 | 2.2435e-08 | 0.030914 | 30227.0945 | 0.055407 | 0.83254 | 0.0006114 | 0.57285 | 1.3152e-06 | 0.78655 | 51477.6443 | 0.16838 | 0.88431 | 0.043265 |  | 0.044892
0.56731 | 7.244e-07 | 0.76547 | 20227.5364 | 0.78672 | 0.91099 | 0.012323 |  | 0.91744 | 1.9085e-07 | 0.42266 | 42233.9134 | 0.6091 | 0.92641 | 0.0049639 | 0.32961 | 9.4474e-07 | 0.80714 | 52233.5943 | 0.72473 | 0.95193 | 0.027466 |  | 0.044752
0.005242 | 4.0357e-08 | 0.09105 | 13401.6981 | 0.13554 | 0.80282 | 0.00091421 |  | 0.12284 | 1.9496e-08 | 0.26911 | 38828.1158 | 0.53931 | 0.91935 | 0.00048572 | 0.30509 | 9.0888e-07 | 0.26838 | 38810.8219 | 0.88182 | 0.96836 | 0.019598 |  | 0.020998
0.062508 | 1.5356e-07 | 0.57618 | 18186.2966 | 0.87397 | 0.92563 | 0.0022929 |  | 0.50012 | 6.754e-08 | 0.7503 | 50266.0148 | 0.10059 | 0.85138 | 0.0023245 | 0.29794 | 8.9838e-07 | 0.050953 | 31661.7162 | 0.70771 | 0.95031 | 0.017426 |  | 0.022044
0.66577 | 8.6964e-07 | 0.73377 | 19827.9685 | 0.29841 | 0.8404 | 0.019404 |  | 0.27325 | 3.7387e-08 | 0.25938 | 38597.737 | 0.4817 | 0.91333 | 0.00094285 | 0.37496 | 1.0108e-06 | 0.67797 | 48165.8753 | 0.66552 | 0.94631 | 0.02779 |  | 0.048137
0.76685 | 1.0608e-06 | 0.30078 | 15765.3389 | 0.94016 | 0.94068 | 0.013379 |  | 0.078228 | 1.3894e-08 | 0.3467 | 40584.8496 | 0.86378 | 0.95378 | 0.00032516 | 0.59672 | 1.3561e-06 | 0.34642 | 40578.6212 | 0.38609 | 0.91784 | 0.035013 |  | 0.048717
0.3957 | 5.1905e-07 | 0.13795 | 14073.9657 | 0.14669 | 0.80625 | 0.011754 |  | 0.59816 | 8.3745e-08 | 0.79666 | 51841.7773 | 0.30786 | 0.8926 | 0.0027255 | 0.33635 | 9.5457e-07 | 0.45754 | 42987.8192 | 0.66009 | 0.94579 | 0.023938 |  | 0.038418
0.67266 | 8.8102e-07 | 0.52392 | 17712.0496 | 0.44364 | 0.8635 | 0.017272 |  | 0.66114 | 9.5999e-08 | 0.48251 | 43531.0523 | 0.013889 | 0.79341 | 0.0033951 | 0.4075 | 1.0584e-06 | 0.45362 | 42903.0389 | 0.79528 | 0.95887 | 0.025584 |  | 0.046252
0.39468 | 5.1794e-07 | 0.26646 | 15448.8529 | 0.9369 | 0.93977 | 0.0064927 |  | 0.96586 | 2.472e-07 | 0.83438 | 53333.5836 | 0.26621 | 0.8866 | 0.0083001 | 0.066196 | 4.9067e-07 | 0.46359 | 43119.033 | 0.82777 | 0.96224 | 0.011802 |  | 0.026595
0.97171 | 2.0645e-06 | 0.9246 | 23326.4182 | 0.53179 | 0.87581 | 0.043548 |  | 0.26381 | 3.6254e-08 | 0.9299 | 58982.9419 | 0.3045 | 0.89214 | 0.0012964 | 0.41471 | 1.069e-06 | 0.035392 | 30596.0727 | 0.64475 | 0.94434 | 0.020656 |  | 0.0655
0.37187 | 4.9327e-07 | 0.22793 | 15076.08 | 0.017683 | 0.72804 | 0.014459 |  | 0.34034 | 4.5629e-08 | 0.96987 | 63945.2858 | 0.56954 | 0.92243 | 0.0016558 | 0.4946 | 1.1893e-06 | 0.88899 | 56063.1936 | 0.8606 | 0.96586 | 0.035757 |  | 0.051871
0.47159 | 6.0474e-07 | 0.56245 | 18059.6594 | 0.14151 | 0.80468 | 0.014741 |  | 0.023773 | 5.9466e-09 | 0.23156 | 37920.8629 | 0.692 | 0.93473 | 0.00013939 | 0.6684 | 1.4886e-06 | 0.18588 | 36730.5324 | 0.32843 | 0.9107 | 0.036542 |  | 0.051423
0.98958 | 2.5079e-06 | 0.060753 | 12839.7728 | 0.63901 | 0.89022 | 0.03845 |  | 0.61096 | 8.6097e-08 | 0.44791 | 42779.4091 | 0.79897 | 0.94602 | 0.0021493 | 0.23598 | 8.0552e-07 | 0.67519 | 48091.3424 | 0.58352 | 0.9385 | 0.022518 |  | 0.063117
0.28997 | 4.0716e-07 | 0.32241 | 15959.4866 | 0.56337 | 0.88008 | 0.0071364 |  | 0.28932 | 3.9328e-08 | 0.36583 | 41003.7186 | 0.79978 | 0.94611 | 0.00094852 | 0.32396 | 9.3649e-07 | 0.25328 | 38451.7509 | 0.49719 | 0.92996 | 0.022489 |  | 0.030574
0.91495 | 1.5572e-06 | 0.85968 | 21715.3652 | 0.1809 | 0.81566 | 0.038936 |  | 0.91991 | 1.9281e-07 | 0.13996 | 35380.0217 | 0.96292 | 0.97062 | 0.0038069 | 0.52272 | 1.2334e-06 | 0.074641 | 32911.7651 | 0.40269 | 0.91977 | 0.027336 |  | 0.070079
0.31704 | 4.353e-07 | 0.88795 | 22317.8707 | 0.71976 | 0.90125 | 0.0081433 |  | 0.15526 | 2.3395e-08 | 0.52451 | 44457.8437 | 0.7937 | 0.94543 | 0.00060351 | 0.6711 | 1.494e-06 | 0.20195 | 37162.8752 | 0.69821 | 0.9494 | 0.032977 |  | 0.041724
0.91889 | 1.5796e-06 | 0.17677 | 14536.9895 | 0.53112 | 0.87572 | 0.027251 |  | 0.83285 | 1.4453e-07 | 0.25062 | 38387.7287 | 0.37173 | 0.90085 | 0.0037543 | 0.17616 | 7.1007e-07 | 0.82512 | 52945.0927 | 0.72769 | 0.95222 | 0.020871 |  | 0.051876
0.083234 | 1.8141e-07 | 0.057862 | 12777.0413 | 0.17451 | 0.81401 | 0.003899 |  | 0.79788 | 1.3175e-07 | 0.1974 | 37041.998 | 0.78711 | 0.9447 | 0.0029435 | 0.65448 | 1.4615e-06 | 0.70091 | 48796.0105 | 0.033368 | 0.83107 | 0.051262 |  | 0.058104
0.14433 | 2.537e-07 | 0.19829 | 14771.4119 | 0.95551 | 0.94545 | 0.0029839 |  | 0.74565 | 1.1606e-07 | 0.52219 | 44406.0907 | 0.21283 | 0.87782 | 0.0035042 | 0.56156 | 1.2964e-06 | 0.55204 | 45078.6752 | 0.75712 | 0.95507 | 0.033009 |  | 0.039497
0.86166 | 1.3231e-06 | 0.16471 | 14399.3911 | 0.55302 | 0.87869 | 0.02243 |  | 0.76523 | 1.2156e-07 | 0.72471 | 49482.6144 | 0.7483 | 0.94053 | 0.003462 | 0.86449 | 2.017e-06 | 0.97979 | 66164.6769 | 0.89718 | 0.97028 | 0.069995 |  | 0.095888
0.72489 | 9.7431e-07 | 0.52377 | 17710.6852 | 0.67321 | 0.89484 | 0.016696 |  | 0.30561 | 4.1316e-08 | 0.2493 | 38355.7356 | 0.15201 | 0.86548 | 0.0011727 | 0.96022 | 2.6397e-06 | 0.90077 | 56794.3126 | 0.87924 | 0.96805 | 0.079954 |  | 0.097823
0.10256 | 2.0547e-07 | 0.43606 | 16946.3683 | 0.34114 | 0.84774 | 0.0042165 |  | 0.30464 | 4.1197e-08 | 0.6158 | 46578.5007 | 0.060866 | 0.83541 | 0.0013955 | 0.15698 | 6.7734e-07 | 0.95256 | 61330.4537 | 0.27566 | 0.90336 | 0.024497 |  | 0.030109
0.6443 | 8.3537e-07 | 0.18627 | 14642.0539 | 0.73764 | 0.90378 | 0.012569 |  | 0.37157 | 4.9613e-08 | 0.66161 | 47732.6622 | 0.64582 | 0.93008 | 0.0014051 | 0.16735 | 6.952e-07 | 0.58908 | 45937.5021 | 0.59068 | 0.93919 | 0.0187 |  | 0.032674
0.092257 | 1.9283e-07 | 0.53789 | 17836.8464 | 0.12423 | 0.7991 | 0.0047678 |  | 0.80997 | 1.3592e-07 | 0.56013 | 45263.6864 | 0.47704 | 0.91283 | 0.0038458 | 0.36904 | 1.0022e-06 | 0.98121 | 66561.9452 | 0.67165 | 0.94689 | 0.036244 |  | 0.044858
0.39692 | 5.2038e-07 | 0.69683 | 19400.6294 | 0.55337 | 0.87874 | 0.0099635 |  | 0.46707 | 6.2643e-08 | 0.71127 | 49090.3907 | 0.439 | 0.90867 | 0.0018983 | 0.77961 | 1.742e-06 | 0.24668 | 38292.2633 | 0.82166 | 0.9616 | 0.037931 |  | 0.049793
0.96155 | 1.9254e-06 | 0.80851 | 20836.9046 | 0.52786 | 0.87528 | 0.038595 |  | 0.66116 | 9.6003e-08 | 0.56137 | 45292.03 | 0.43147 | 0.90783 | 0.0027488 | 0.089134 | 5.4553e-07 | 0.52163 | 44393.5377 | 0.52584 | 0.93286 | 0.014505 |  | 0.055848
0.025905 | 9.3962e-08 | 0.23576 | 15153.7113 | 0.078893 | 0.78069 | 0.002361 |  | 0.27746 | 3.7894e-08 | 0.62821 | 46883.6826 | 0.35407 | 0.89866 | 0.0011347 | 0.45124 | 1.1233e-06 | 0.62208 | 46732.2394 | 0.19531 | 0.88984 | 0.034195 |  | 0.037691
0.88497 | 1.4128e-06 | 0.99442 | 29070.9683 | 0.85551 | 0.92223 | 0.028564 |  | 0.67836 | 9.9693e-08 | 0.70714 | 48972.3395 | 0.051152 | 0.83012 | 0.00351 | 0.39721 | 1.0433e-06 | 0.37796 | 41267.6401 | 0.56641 | 0.93685 | 0.025939 |  | 0.058013
0.69069 | 9.1172e-07 | 0.4118 | 16737.6642 | 0.55379 | 0.87879 | 0.016386 |  | 0.13593 | 2.1081e-08 | 0.22709 | 37809.0686 | 0.97128 | 0.97291 | 0.00043774 | 0.33742 | 9.5613e-07 | 0.72144 | 49386.1968 | 0.23842 | 0.89754 | 0.029773 |  | 0.046596
0.20768 | 3.2176e-07 | 0.31986 | 15936.7543 | 0.034588 | 0.75043 | 0.0089583 |  | 0.0953 | 1.6086e-08 | 0.061422 | 32254.4444 | 0.73326 | 0.93895 | 0.00032961 | 0.47549 | 1.16e-06 | 0.9446 | 60410.3066 | 0.51266 | 0.93153 | 0.039595 |  | 0.048883
0.50269 | 6.4191e-07 | 0.89291 | 22436.1512 | 0.81406 | 0.91525 | 0.011356 |  | 0.76043 | 1.2017e-07 | 0.31438 | 39867.0904 | 0.32883 | 0.89542 | 0.0032459 | 0.90362 | 2.1983e-06 | 0.24235 | 38186.8535 | 0.63215 | 0.94315 | 0.050534 |  | 0.065136
0.34608 | 4.658e-07 | 0.46982 | 17237.7357 | 0.45744 | 0.86548 | 0.0089637 |  | 0.41699 | 5.5629e-08 | 0.10183 | 34055.9018 | 0.35236 | 0.89845 | 0.0013459 | 0.2312 | 7.9818e-07 | 0.62759 | 46868.3467 | 0.70775 | 0.95031 | 0.02125 |  | 0.031559
0.55894 | 7.1325e-07 | 0.81539 | 20943.5766 | 0.73661 | 0.90363 | 0.01277 |  | 0.9167 | 1.9027e-07 | 0.55255 | 45090.3285 | 0.97992 | 0.97577 | 0.0045897 | 0.48219 | 1.1702e-06 | 0.95443 | 61567.5062 | 0.64432 | 0.9443 | 0.039726 |  | 0.057086
0.58924 | 7.5437e-07 | 0.78203 | 20451.4904 | 0.87738 | 0.92628 | 0.012017 |  | 0.35019 | 4.6873e-08 | 0.13489 | 35217.053 | 0.54397 | 0.91983 | 0.0010884 | 0.84796 | 1.9539e-06 | 0.96852 | 63697.8593 | 0.44166 | 0.92412 | 0.070495 |  | 0.0836
0.84108 | 1.2547e-06 | 0.8382 | 21320.4208 | 0.83058 | 0.91794 | 0.021297 |  | 0.0071258 | 2.6022e-09 | 0.45232 | 42874.7632 | 0.85958 | 0.95324 | 6.3835e-05 | 0.24248 | 8.1548e-07 | 0.58933 | 45943.3648 | 0.72438 | 0.9519 | 0.021268 |  | 0.042629
0.97194 | 2.0682e-06 | 0.46755 | 17218.0531 | 0.45321 | 0.86487 | 0.03988 |  | 0.14387 | 2.2035e-08 | 0.80466 | 52139.3685 | 0.55949 | 0.92141 | 0.00068099 | 0.99028 | 3.2891e-06 | 0.20728 | 37302.8151 | 0.27171 | 0.90278 | 0.083395 |  | 0.12396
0.38919 | 5.1196e-07 | 0.53365 | 17798.8689 | 0.85376 | 0.92192 | 0.0077022 |  | 0.23495 | 3.2816e-08 | 0.89923 | 56694.7553 | 0.13523 | 0.86138 | 0.0011998 | 0.23099 | 7.9786e-07 | 0.2442 | 38232.0873 | 0.67763 | 0.94745 | 0.018123 |  | 0.027025
0.11008 | 2.1447e-07 | 0.99557 | 29539.3057 | 0.35403 | 0.84985 | 0.0055131 |  | 0.83134 | 1.4393e-07 | 0.20661 | 37285.1784 | 0.27049 | 0.88724 | 0.0038023 | 0.4377 | 1.1031e-06 | 0.34468 | 40540.3812 | 0.12399 | 0.87335 | 0.031765 |  | 0.041081
0.84963 | 1.2821e-06 | 0.85457 | 21617.2881 | 0.34127 | 0.84776 | 0.028845 |  | 0.72327 | 1.1022e-07 | 0.67549 | 48099.4644 | 0.20815 | 0.87698 | 0.0035126 | 0.15642 | 6.7636e-07 | 0.19136 | 36879.7767 | 0.62672 | 0.94263 | 0.015155 |  | 0.047513
0.85187 | 1.2895e-06 | 0.94721 | 24189.7822 | 0.080145 | 0.7813 | 0.036889 |  | 0.46124 | 6.1802e-08 | 0.89719 | 56564.6759 | 0.51376 | 0.91671 | 0.0020533 | 0.72276 | 1.6029e-06 | 0.1189 | 34679.4472 | 0.91703 | 0.97295 | 0.03084 |  | 0.069782
0.55941 | 7.1387e-07 | 0.84746 | 21485.2728 | 0.32942 | 0.84579 | 0.01613 |  | 0.67644 | 9.9274e-08 | 0.72024 | 49350.9479 | 0.28512 | 0.8894 | 0.0031405 | 0.43944 | 1.1056e-06 | 0.1621 | 36055.8517 | 0.34242 | 0.91251 | 0.026663 |  | 0.045933
0.081402 | 1.7904e-07 | 0.92398 | 23306.2629 | 0.50775 | 0.87252 | 0.0038198 |  | 0.2542 | 3.5105e-08 | 0.86562 | 54785.6122 | 0.21083 | 0.87746 | 0.0012206 | 0.84202 | 1.9326e-06 | 0.82876 | 53095.997 | 0.58766 | 0.9389 | 0.058516 |  | 0.063557
0.41564 | 5.4098e-07 | 0.98636 | 27213.6433 | 0.49205 | 0.87035 | 0.012551 |  | 0.60997 | 8.5912e-08 | 0.69972 | 48762.6085 | 0.97183 | 0.97308 | 0.0022409 | 0.4299 | 1.0915e-06 | 0.50755 | 44080.977 | 0.99229 | 0.98935 | 0.024818 |  | 0.03961
0.59975 | 7.6917e-07 | 0.29505 | 15713.3188 | 0.4877 | 0.86975 | 0.014032 |  | 0.50123 | 6.771e-08 | 0.50814 | 44094.1763 | 0.29757 | 0.89117 | 0.0019758 | 0.40996 | 1.062e-06 | 0.048783 | 31528.4444 | 0.77019 | 0.95635 | 0.020072 |  | 0.03608
0.56997 | 7.2798e-07 | 0.084275 | 13288.105 | 0.22854 | 0.82675 | 0.015047 |  | 0.44485 | 5.9476e-08 | 0.79424 | 51753.4214 | 0.7856 | 0.94453 | 0.0017427 | 0.77351 | 1.7258e-06 | 0.84032 | 53591.9575 | 0.48335 | 0.92854 | 0.053743 |  | 0.070532
0.32739 | 4.4613e-07 | 0.37956 | 16459.7034 | 0.35483 | 0.84998 | 0.0089838 |  | 0.044135 | 9.1857e-09 | 0.92324 | 58421.5038 | 0.7269 | 0.9383 | 0.00030141 | 0.3406 | 9.6076e-07 | 0.22431 | 37739.3642 | 0.63411 | 0.94333 | 0.021871 |  | 0.031156
0.67443 | 8.8397e-07 | 0.98294 | 26734.7214 | 0.7548 | 0.90625 | 0.017968 |  | 0.53619 | 7.3178e-08 | 0.17105 | 36315.1937 | 0.6196 | 0.92746 | 0.0016974 | 0.48853 | 1.1799e-06 | 0.74791 | 50190.8419 | 0.054188 | 0.84596 | 0.040971 |  | 0.060637
0.38176 | 5.0392e-07 | 0.50382 | 17534.3365 | 0.7601 | 0.90702 | 0.0081116 |  | 0.79242 | 1.2995e-07 | 0.59576 | 46095.8234 | 0.019645 | 0.80274 | 0.0046497 | 0.50156 | 1.2001e-06 | 0.0045426 | 26061.9861 | 0.98984 | 0.98821 | 0.016693 |  | 0.029455
0.55849 | 7.1266e-07 | 0.86165 | 21753.9864 | 0.15426 | 0.80847 | 0.018224 |  | 0.073746 | 1.3304e-08 | 0.064077 | 32393.5878 | 0.87236 | 0.95491 | 0.00025832 | 0.16455 | 6.9042e-07 | 0.51701 | 44290.6824 | 0.85352 | 0.96506 | 0.016869 |  | 0.035351
0.68952 | 9.0969e-07 | 0.63642 | 18765.5664 | 0.15235 | 0.80792 | 0.022203 |  | 0.7721 | 1.2359e-07 | 0.067601 | 32572.3825 | 0.81985 | 0.9484 | 0.0024677 | 0.81506 | 1.8438e-06 | 0.5994 | 46182.6038 | 0.9183 | 0.97313 | 0.045773 |  | 0.070443
0.81813 | 1.1874e-06 | 0.228 | 15076.7224 | 0.11826 | 0.79703 | 0.028246 |  | 0.5933 | 8.287e-08 | 0.25304 | 38446.0615 | 0.52641 | 0.91802 | 0.0020575 | 0.52454 | 1.2363e-06 | 0.26147 | 38647.4956 | 0.20136 | 0.89099 | 0.03309 |  | 0.063394
0.75925 | 1.0442e-06 | 0.74198 | 19928.235 | 0.063957 | 0.77264 | 0.028836 |  | 0.84399 | 1.4913e-07 | 0.71553 | 49213.3881 | 0.51206 | 0.91653 | 0.0044537 | 0.75749 | 1.6849e-06 | 0.37225 | 41143.4206 | 0.77413 | 0.95674 | 0.039546 |  | 0.072836
0.99268 | 2.662e-06 | 0.32682 | 15998.6585 | 0.84144 | 0.91977 | 0.038293 |  | 0.75972 | 1.1997e-07 | 0.50703 | 44069.4957 | 0.74067 | 0.93973 | 0.0031177 | 0.78003 | 1.7431e-06 | 0.69808 | 48716.5969 | 0.95141 | 0.97839 | 0.044841 |  | 0.086252
0.19642 | 3.0992e-07 | 0.76288 | 20193.5809 | 0.078275 | 0.78038 | 0.0084044 |  | 0.77589 | 1.2474e-07 | 0.66289 | 47766.1128 | 0.32698 | 0.89518 | 0.0038122 | 0.074783 | 5.1219e-07 | 0.88214 | 55667.1967 | 0.81672 | 0.96108 | 0.015448 |  | 0.027664
0.61427 | 7.9009e-07 | 0.88348 | 22214.8307 | 0.59709 | 0.88461 | 0.01575 |  | 0.13043 | 2.0418e-08 | 0.27832 | 39043.4406 | 0.90064 | 0.9589 | 0.00045572 | 0.42961 | 1.091e-06 | 0.95012 | 61035.0561 | 0.049957 | 0.84342 | 0.043048 |  | 0.059253
0.47052 | 6.0348e-07 | 0.025128 | 11830.6091 | 0.20361 | 0.82118 | 0.012385 |  | 0.17237 | 2.5424e-08 | 0.74567 | 50120.4968 | 0.19904 | 0.87529 | 0.00083543 | 0.44312 | 1.1111e-06 | 0.13025 | 35064.9535 | 0.8224 | 0.96167 | 0.022465 |  | 0.035685
0.25974 | 3.7586e-07 | 0.16644 | 14419.4743 | 0.11693 | 0.79655 | 0.0088572 |  | 0.95115 | 2.2451e-07 | 0.17044 | 36297.8225 | 0.018678 | 0.80136 | 0.0071719 | 0.86784 | 2.0306e-06 | 0.18502 | 36706.8275 | 0.23739 | 0.89737 | 0.051701 |  | 0.06773
0.21286 | 3.2718e-07 | 0.086504 | 13326.102 | 0.13707 | 0.8033 | 0.0073888 |  | 0.26906 | 3.6883e-08 | 0.36644 | 41016.9324 | 0.36164 | 0.89961 | 0.0010048 | 0.65425 | 1.461e-06 | 0.66675 | 47867.4595 | 0.1755 | 0.88583 | 0.045588 |  | 0.053982
0.63637 | 8.2314e-07 | 0.9391 | 23848.0448 | 0.91016 | 0.93311 | 0.013982 |  | 0.10739 | 1.7599e-08 | 0.58308 | 45796.2225 | 0.32943 | 0.8955 | 0.00052197 | 0.046325 | 4.3435e-07 | 0.83543 | 53378.7281 | 0.70434 | 0.94999 | 0.012916 |  | 0.027419
0.95436 | 1.8471e-06 | 0.49569 | 17463.0194 | 0.35958 | 0.85074 | 0.037871 |  | 0.61565 | 8.6974e-08 | 0.90796 | 57276.9535 | 0.03192 | 0.8163 | 0.0034329 | 0.76053 | 1.6925e-06 | 0.28301 | 39152.4239 | 0.84808 | 0.96445 | 0.037225 |  | 0.078528
0.86917 | 1.3503e-06 | 0.56633 | 18095.265 | 0.23218 | 0.82753 | 0.030512 |  | 0.25261 | 3.4915e-08 | 0.99308 | 71847.5695 | 0.69828 | 0.93536 | 0.0013709 | 0.11732 | 6.0428e-07 | 0.0082211 | 27179.272 | 0.84434 | 0.96404 | 0.0098203 |  | 0.041703
0.56395 | 7.199e-07 | 0.56424 | 18076.0676 | 0.76054 | 0.90708 | 0.011762 |  | 0.74541 | 1.1599e-07 | 0.80141 | 52017.3375 | 0.055407 | 0.83254 | 0.0042132 | 0.096796 | 5.6226e-07 | 0.68723 | 48416.842 | 0.1919 | 0.88917 | 0.017562 |  | 0.033536
0.53129 | 6.7745e-07 | 0.97711 | 26094.1322 | 0.54662 | 0.87782 | 0.015009 |  | 0.45132 | 6.0388e-08 | 0.65429 | 47542.8231 | 0.16784 | 0.86902 | 0.0019404 | 0.62731 | 1.4106e-06 | 0.32933 | 40200.9605 | 0.54567 | 0.93482 | 0.03456 |  | 0.051509
0.020037 | 8.1778e-08 | 0.10099 | 13559.1037 | 0.74312 | 0.90456 | 0.0011852 |  | 0.44429 | 5.9397e-08 | 0.57455 | 45596.8557 | 0.90243 | 0.95917 | 0.0015113 | 0.93519 | 2.4006e-06 | 0.010485 | 27675.2032 | 0.82746 | 0.96221 | 0.03991 |  | 0.042607
0.36247 | 4.8322e-07 | 0.08127 | 13235.848 | 0.27544 | 0.83617 | 0.0096088 |  | 0.34978 | 4.6821e-08 | 0.37915 | 41293.2692 | 0.0012462 | 0.73461 | 0.0017986 | 0.34094 | 9.6126e-07 | 0.6085 | 46401.3891 | 0.98817 | 0.98752 | 0.023074 |  | 0.034482
0.67136 | 8.7886e-07 | 0.60853 | 18492.1141 | 0.16168 | 0.81056 | 0.021171 |  | 0.43075 | 5.7513e-08 | 0.13894 | 35347.4735 | 0.40212 | 0.90447 | 0.0014006 | 0.66745 | 1.4867e-06 | 0.55366 | 45115.6702 | 0.52505 | 0.93278 | 0.040038 |  | 0.06261
0.25851 | 3.7459e-07 | 0.74935 | 20020.0354 | 0.72368 | 0.9018 | 0.0066037 |  | 0.28411 | 3.8697e-08 | 0.39399 | 41614.933 | 0.81347 | 0.94766 | 0.00094047 | 0.21213 | 7.6842e-07 | 0.54081 | 44823.8446 | 0.95871 | 0.97977 | 0.018235 |  | 0.025779
0.22663 | 3.4154e-07 | 0.63798 | 18781.2144 | 0.40158 | 0.85728 | 0.0070196 |  | 0.77472 | 1.2438e-07 | 0.51331 | 44208.5942 | 0.77489 | 0.94336 | 0.0032108 | 0.62975 | 1.4151e-06 | 0.91264 | 57609.4261 | 0.031441 | 0.82929 | 0.054964 |  | 0.065195
0.61036 | 7.844e-07 | 0.050174 | 12598.9223 | 0.47446 | 0.86789 | 0.013366 |  | 0.35589 | 4.7598e-08 | 0.20311 | 37193.3266 | 0.0053701 | 0.7691 | 0.0016435 | 0.19899 | 7.4749e-07 | 0.41906 | 42156.2524 | 0.53782 | 0.93405 | 0.019035 |  | 0.034045
0.59843 | 7.673e-07 | 0.083221 | 13269.9159 | 0.17988 | 0.8154 | 0.016559 |  | 0.56522 | 7.7975e-08 | 0.46496 | 43148.7466 | 0.51508 | 0.91685 | 0.0021104 | 0.033191 | 3.892e-07 | 0.39952 | 41734.5122 | 0.089176 | 0.8621 | 0.011703 |  | 0.030373
0.58293 | 7.4564e-07 | 0.86471 | 21814.934 | 0.71523 | 0.90062 | 0.013816 |  | 0.072521 | 1.3142e-08 | 0.25035 | 38381.1781 | 0.30056 | 0.89159 | 0.00034967 | 0.97067 | 2.7847e-06 | 0.017943 | 28864.1947 | 0.67675 | 0.94737 | 0.050913 |  | 0.065079
0.38402 | 5.0636e-07 | 0.62506 | 18652.9537 | 0.029516 | 0.74499 | 0.01483 |  | 0.78554 | 1.2773e-07 | 0.59762 | 46140.0852 | 0.87187 | 0.95485 | 0.003319 | 0.44259 | 1.1104e-06 | 0.59908 | 46174.8637 | 0.85954 | 0.96574 | 0.028089 |  | 0.046238
0.64602 | 8.3806e-07 | 0.34929 | 16196.5299 | 0.11003 | 0.79402 | 0.02051 |  | 0.76093 | 1.2032e-07 | 0.4927 | 43753.9753 | 0.58306 | 0.92379 | 0.0032348 | 0.93102 | 2.3694e-06 | 0.38874 | 41501.2127 | 0.29791 | 0.90657 | 0.063964 |  | 0.087709
0.49246 | 6.2953e-07 | 0.33158 | 16040.7575 | 0.76815 | 0.9082 | 0.0096479 |  | 0.54068 | 7.3903e-08 | 0.7468 | 50155.9114 | 0.21488 | 0.87819 | 0.0024162 | 0.40823 | 1.0595e-06 | 0.67802 | 48167.2794 | 0.55287 | 0.93553 | 0.029855 |  | 0.041919
0.86854 | 1.348e-06 | 0.8283 | 21152.0409 | 0.49555 | 0.87084 | 0.027667 |  | 0.92952 | 2.0105e-07 | 0.67964 | 48210.811 | 0.48028 | 0.91318 | 0.0059548 | 0.54523 | 1.2695e-06 | 0.19589 | 37001.8655 | 0.46787 | 0.92692 | 0.029898 |  | 0.06352
0.20664 | 3.2067e-07 | 0.649 | 18892.5382 | 0.25578 | 0.83237 | 0.0072302 |  | 0.17631 | 2.589e-08 | 0.80512 | 52156.6878 | 0.54114 | 0.91954 | 0.00080333 | 0.80484 | 1.8129e-06 | 0.35382 | 40741.0675 | 0.864 | 0.96625 | 0.041044 |  | 0.049078
0.09027 | 1.9034e-07 | 0.61633 | 18567.5903 | 0.042032 | 0.75728 | 0.0053853 |  | 0.37417 | 4.9949e-08 | 0.67349 | 48046.1059 | 0.46148 | 0.91115 | 0.0014821 | 0.81938 | 1.8573e-06 | 0.45625 | 42959.9519 | 0.21313 | 0.89317 | 0.053014 |  | 0.059881
0.24236 | 3.5787e-07 | 0.39742 | 16613.9141 | 0.72167 | 0.90152 | 0.0057673 |  | 0.26687 | 3.662e-08 | 0.056584 | 31989.9737 | 0.2619 | 0.88594 | 0.00088484 | 0.83489 | 1.908e-06 | 0.18152 | 36610.3448 | 0.22182 | 0.89471 | 0.048847 |  | 0.055499
0.14408 | 2.5343e-07 | 0.68164 | 19234.451 | 0.36663 | 0.85187 | 0.0053647 |  | 0.40874 | 5.4514e-08 | 0.2832 | 39156.8002 | 0.72388 | 0.93798 | 0.0012973 | 0.66507 | 1.482e-06 | 0.01394 | 28288.4057 | 0.31385 | 0.90876 | 0.030895 |  | 0.037557
0.91289 | 1.5458e-06 | 0.27327 | 15512.5987 | 0.49908 | 0.87133 | 0.027872 |  | 0.94713 | 2.1947e-07 | 0.49148 | 43727.2912 | 0.31513 | 0.89359 | 0.0063336 | 0.26936 | 8.5603e-07 | 0.21804 | 37580.3117 | 0.60863 | 0.94091 | 0.019565 |  | 0.053771
0.21151 | 3.2577e-07 | 0.66327 | 19039.6643 | 0.004883 | 0.68908 | 0.01101 |  | 0.88236 | 1.6778e-07 | 0.10365 | 34125.2587 | 0.65854 | 0.93136 | 0.0036752 | 0.51599 | 1.2227e-06 | 0.15877 | 35957.4862 | 0.87281 | 0.96728 | 0.024768 |  | 0.039453
0.60351 | 7.7453e-07 | 0.19251 | 14709.7441 | 0.89743 | 0.93033 | 0.010027 |  | 0.28795 | 3.9162e-08 | 0.56208 | 45308.3926 | 0.063484 | 0.83671 | 0.0013025 | 0.089889 | 5.4721e-07 | 0.85038 | 54046.9809 | 0.56489 | 0.9367 | 0.016886 |  | 0.028215
0.61087 | 7.8515e-07 | 0.63257 | 18727.1915 | 0.85 | 0.92126 | 0.012189 |  | 0.075122 | 1.3486e-08 | 0.31457 | 39871.2178 | 0.45206 | 0.91012 | 0.00035088 | 0.40408 | 1.0534e-06 | 0.64541 | 47315.467 | 0.2796 | 0.90395 | 0.031391 |  | 0.04393
0.29321 | 4.1051e-07 | 0.51141 | 17601.1737 | 0.38648 | 0.85497 | 0.008304 |  | 0.71067 | 1.0712e-07 | 0.73383 | 49755.9698 | 0.8671 | 0.95422 | 0.0029726 | 0.40024 | 1.0478e-06 | 0.90744 | 57241.6137 | 0.3616 | 0.9149 | 0.035246 |  | 0.046523
0.39347 | 5.1662e-07 | 0.2263 | 15059.7563 | 0.70589 | 0.89932 | 0.0080547 |  | 0.92368 | 1.9592e-07 | 0.96397 | 62927.3292 | 0.73487 | 0.93912 | 0.006834 | 0.079618 | 5.2375e-07 | 0.028585 | 30019.4066 | 0.054547 | 0.84617 | 0.01371 |  | 0.028598
0.45257 | 5.8265e-07 | 0.081049 | 13231.9483 | 0.57965 | 0.88227 | 0.0094099 |  | 0.953 | 2.2695e-07 | 0.68266 | 48292.3031 | 0.064032 | 0.83697 | 0.0078278 | 0.7878 | 1.7643e-06 | 0.53823 | 44765.6185 | 0.20465 | 0.89161 | 0.05196 |  | 0.069198
0.54318 | 6.9266e-07 | 0.57056 | 18134.309 | 0.011674 | 0.71496 | 0.021786 |  | 0.030878 | 7.1377e-09 | 0.1393 | 35359.0205 | 0.16744 | 0.86893 | 0.0001916 | 0.48124 | 1.1687e-06 | 0.65208 | 47485.7873 | 0.54915 | 0.93516 | 0.032588 |  | 0.054565
0.39326 | 5.164e-07 | 0.039578 | 12318.7593 | 0.45717 | 0.86544 | 0.0088397 |  | 0.11962 | 1.9104e-08 | 0.41728 | 42117.9672 | 0.064899 | 0.83739 | 0.00060902 | 0.82533 | 1.8763e-06 | 0.50608 | 44048.545 | 0.63954 | 0.94385 | 0.048233 |  | 0.057682
0.79924 | 1.1375e-06 | 0.94783 | 24217.6136 | 0.58399 | 0.88285 | 0.023833 |  | 0.76619 | 1.2184e-07 | 0.34272 | 40497.3318 | 0.084496 | 0.84571 | 0.0037332 | 0.96963 | 2.7683e-06 | 0.77094 | 50939.1554 | 0.57749 | 0.93792 | 0.081185 |  | 0.10875
0.75808 | 1.0417e-06 | 0.31032 | 15851.3699 | 0.49894 | 0.87131 | 0.018937 |  | 0.42779 | 5.7104e-08 | 0.79543 | 51796.674 | 0.70659 | 0.93621 | 0.0017037 | 0.12391 | 6.1705e-07 | 0.59437 | 46062.7527 | 0.08101 | 0.85891 | 0.019833 |  | 0.040474
0.75244 | 1.0297e-06 | 0.6416 | 18817.6013 | 0.10658 | 0.79271 | 0.026378 |  | 0.92148 | 1.9409e-07 | 0.40296 | 41808.7674 | 0.47213 | 0.9123 | 0.0051925 | 0.42738 | 1.0877e-06 | 0.92069 | 58217.7097 | 0.86065 | 0.96587 | 0.033834 |  | 0.065405
0.57229 | 7.3111e-07 | 0.092778 | 13429.8056 | 0.89239 | 0.92927 | 0.0090917 |  | 0.70377 | 1.0548e-07 | 0.75199 | 50319.8938 | 0.92998 | 0.96369 | 0.0028929 | 0.5816 | 1.33e-06 | 0.27023 | 38854.3651 | 0.95812 | 0.97966 | 0.027683 |  | 0.039668
0.87367 | 1.3674e-06 | 0.050963 | 12618.0394 | 0.14427 | 0.80552 | 0.030245 |  | 0.39296 | 5.2409e-08 | 0.62491 | 46801.9209 | 0.47255 | 0.91235 | 0.0015213 | 0.57528 | 1.3193e-06 | 0.84788 | 53931.6496 | 0.89792 | 0.97038 | 0.037946 |  | 0.069712
0.36589 | 4.8687e-07 | 0.67831 | 19198.7057 | 0.3096 | 0.84238 | 0.010659 |  | 0.68206 | 1.0051e-07 | 0.90061 | 56783.7992 | 0.38416 | 0.90235 | 0.0034348 | 0.59627 | 1.3553e-06 | 0.75073 | 50279.8277 | 0.87302 | 0.9673 | 0.03684 |  | 0.050934
0.79689 | 1.1315e-06 | 0.77778 | 20392.9051 | 0.71421 | 0.90048 | 0.020254 |  | 0.84791 | 1.5082e-07 | 0.81802 | 52657.9353 | 0.40882 | 0.90525 | 0.0048466 | 0.78405 | 1.754e-06 | 0.87275 | 55154.5363 | 0.22286 | 0.89489 | 0.059435 |  | 0.084536
0.2875 | 4.0459e-07 | 0.90005 | 22615.0268 | 0.75556 | 0.90636 | 0.0074653 |  | 0.4694 | 6.2981e-08 | 0.48933 | 43680.1324 | 0.41127 | 0.90553 | 0.0017667 | 0.055502 | 4.6171e-07 | 0.08542 | 33392.8998 | 0.33502 | 0.91156 | 0.010604 |  | 0.019836
0.60647 | 7.7877e-07 | 0.6216 | 18618.9923 | 0.39168 | 0.85577 | 0.016044 |  | 0.97341 | 2.6293e-07 | 0.058194 | 32079.6617 | 0.45597 | 0.91055 | 0.0059005 | 0.221 | 7.8235e-07 | 0.12889 | 35019.8891 | 0.56722 | 0.93693 | 0.017157 |  | 0.039101
0.43748 | 5.6545e-07 | 0.055449 | 12722.9902 | 0.52108 | 0.87435 | 0.0093688 |  | 0.40837 | 5.4464e-08 | 0.18679 | 36755.5952 | 0.92512 | 0.96283 | 0.0011411 | 0.55826 | 1.2909e-06 | 0.42076 | 42193.1256 | 0.057465 | 0.84782 | 0.040298 |  | 0.050808
0.79267 | 1.1211e-06 | 0.48485 | 17368.3617 | 0.07181 | 0.77705 | 0.029461 |  | 0.15914 | 2.3856e-08 | 0.42837 | 42357.3579 | 0.82239 | 0.9487 | 0.00058653 | 0.68981 | 1.5319e-06 | 0.5807 | 45740.3036 | 0.57516 | 0.9377 | 0.041213 |  | 0.07126
0.024585 | 9.1332e-08 | 0.951 | 24365.3564 | 0.84359 | 0.92014 | 0.0016627 |  | 0.40805 | 5.4422e-08 | 0.30407 | 39634.5371 | 0.43224 | 0.90792 | 0.0014182 | 0.83304 | 1.9017e-06 | 0.36166 | 40912.6239 | 0.55452 | 0.93569 | 0.047114 |  | 0.050195
0.5037 | 6.4314e-07 | 0.16665 | 14421.8823 | 0.93634 | 0.93961 | 0.0077599 |  | 0.37758 | 5.0392e-08 | 0.86695 | 54853.3584 | 0.58164 | 0.92365 | 0.0016136 | 0.714 | 1.5834e-06 | 0.2939 | 39403.008 | 0.040356 | 0.83682 | 0.04874 |  | 0.058113
0.80114 | 1.1423e-06 | 0.83542 | 21272.3784 | 0.47269 | 0.86764 | 0.023786 |  | 0.38321 | 5.1127e-08 | 0.63679 | 47097.5697 | 0.23983 | 0.88244 | 0.001589 | 0.55507 | 1.2856e-06 | 0.69204 | 48549.0604 | 0.70123 | 0.94969 | 0.035304 |  | 0.060679
0.4353 | 5.6299e-07 | 0.21108 | 14905.1685 | 0.77895 | 0.90981 | 0.0082652 |  | 0.9946 | 3.6167e-07 | 0.16725 | 36206.1708 | 0.64267 | 0.92977 | 0.0083126 | 0.63799 | 1.4303e-06 | 0.91701 | 57933.6281 | 0.81172 | 0.96056 | 0.044739 |  | 0.061317
0.81896 | 1.1897e-06 | 0.94098 | 23923.2794 | 0.969 | 0.95058 | 0.018678 |  | 0.29726 | 4.0295e-08 | 0.71801 | 49285.7284 | 0.88991 | 0.95733 | 0.0011012 | 0.67832 | 1.5084e-06 | 0.8572 | 54369.5979 | 0.52668 | 0.93294 | 0.047117 |  | 0.066896
0.37147 | 4.9284e-07 | 0.89738 | 22546.8085 | 0.65965 | 0.893 | 0.0095808 |  | 0.41951 | 5.5971e-08 | 0.86747 | 54879.7572 | 0.32922 | 0.89547 | 0.0018878 | 0.90631 | 2.213e-06 | 0.68656 | 48398.5763 | 0.48859 | 0.92908 | 0.063502 |  | 0.074971
0.81203 | 1.1708e-06 | 0.78426 | 20482.5761 | 0.24636 | 0.83048 | 0.027344 |  | 0.98272 | 2.8986e-07 | 0.41254 | 42015.693 | 0.5454 | 0.91997 | 0.0076341 | 0.35719 | 9.8491e-07 | 0.23016 | 37885.9184 | 0.1669 | 0.88398 | 0.026502 |  | 0.06148
0.61392 | 7.8959e-07 | 0.31071 | 15854.84 | 0.097624 | 0.78914 | 0.019524 |  | 0.51722 | 7.0171e-08 | 0.17556 | 36443.5309 | 0.17228 | 0.86996 | 0.0019117 | 0.054251 | 4.5814e-07 | 0.20999 | 37373.207 | 0.059018 | 0.84866 | 0.013339 |  | 0.034775
0.39314 | 5.1626e-07 | 0.076534 | 13150.8944 | 0.34689 | 0.84869 | 0.009724 |  | 0.9125 | 1.8708e-07 | 0.22 | 37630.1016 | 0.88372 | 0.95646 | 0.0040803 | 0.95013 | 2.5302e-06 | 0.72602 | 49521.5231 | 0.6327 | 0.9432 | 0.07168 |  | 0.085484
0.81004 | 1.1654e-06 | 0.52195 | 17694.4703 | 0.022946 | 0.73654 | 0.034492 |  | 0.95619 | 2.3142e-07 | 0.26916 | 38829.172 | 0.045337 | 0.82651 | 0.0072305 | 0.26638 | 8.5158e-07 | 0.23113 | 37910.0378 | 0.0085784 | 0.79247 | 0.028273 |  | 0.069996
0.36282 | 4.8359e-07 | 0.47874 | 17315.1281 | 0.57758 | 0.88199 | 0.0086917 |  | 0.51815 | 7.0316e-08 | 0.029377 | 30091.3437 | 0.33012 | 0.89559 | 0.0015906 | 0.19883 | 7.4724e-07 | 0.63014 | 46931.587 | 0.47337 | 0.9275 | 0.021009 |  | 0.031291
0.021186 | 8.4271e-08 | 0.3127 | 15872.7519 | 0.025543 | 0.74011 | 0.0024136 |  | 0.99856 | 4.4222e-07 | 0.39001 | 41528.7072 | 0.20232 | 0.8759 | 0.01285 | 0.62748 | 1.4109e-06 | 0.90818 | 57292.2529 | 0.21815 | 0.89406 | 0.049229 |  | 0.064493
0.64602 | 8.3806e-07 | 0.35944 | 16285.1166 | 0.32777 | 0.84551 | 0.017112 |  | 0.97478 | 2.6626e-07 | 0.013051 | 28143.2213 | 0.0013977 | 0.73722 | 0.0088912 | 0.35032 | 9.7491e-07 | 0.76287 | 50671.1339 | 0.47078 | 0.92723 | 0.029117 |  | 0.05512
0.071586 | 1.6608e-07 | 0.60585 | 18466.2973 | 0.8752 | 0.92586 | 0.0024983 |  | 0.14299 | 2.193e-08 | 0.74862 | 50213.1596 | 0.81312 | 0.94762 | 0.00062236 | 0.88825 | 2.1205e-06 | 0.69366 | 48593.6541 | 0.5189 | 0.93216 | 0.060627 |  | 0.063748
0.59758 | 7.6609e-07 | 0.59547 | 18367.2797 | 0.59707 | 0.8846 | 0.013968 |  | 0.33624 | 4.5113e-08 | 0.56558 | 45388.9619 | 0.82081 | 0.94851 | 0.0011746 | 0.013156 | 2.9153e-07 | 0.63881 | 47148.4221 | 0.47148 | 0.9273 | 0.0082295 |  | 0.023372
0.49167 | 6.2858e-07 | 0.77862 | 20404.4664 | 0.35136 | 0.84942 | 0.013739 |  | 0.7635 | 1.2106e-07 | 0.36847 | 41061.0805 | 0.32832 | 0.89536 | 0.003335 | 0.20026 | 7.4953e-07 | 0.32301 | 40060.3386 | 0.80211 | 0.95956 | 0.017061 |  | 0.034135
0.27278 | 3.8935e-07 | 0.65436 | 18947.417 | 0.64403 | 0.8909 | 0.0070072 |  | 0.23735 | 3.3101e-08 | 0.80679 | 52220.1689 | 0.056401 | 0.83308 | 0.001204 | 0.60149 | 1.3644e-06 | 0.84753 | 53915.7523 | 0.71756 | 0.95125 | 0.040815 |  | 0.049026
0.90026 | 1.4814e-06 | 0.070983 | 13046.808 | 0.049943 | 0.76348 | 0.038071 |  | 0.8098 | 1.3586e-07 | 0.81591 | 52573.8737 | 0.3069 | 0.89247 | 0.004467 | 0.073945 | 5.1015e-07 | 0.50277 | 43975.5877 | 0.17263 | 0.88522 | 0.015059 |  | 0.057596
0.59346 | 7.6029e-07 | 0.27688 | 15546.2605 | 0.37543 | 0.85326 | 0.014816 |  | 0.69711 | 1.0392e-07 | 0.020314 | 29159.5236 | 0.86514 | 0.95396 | 0.0018645 | 0.63418 | 1.4232e-06 | 0.32184 | 40034.2157 | 0.76299 | 0.95564 | 0.032756 |  | 0.049436
0.25067 | 3.6647e-07 | 0.63082 | 18709.8541 | 0.29771 | 0.84027 | 0.0080085 |  | 0.67596 | 9.9168e-08 | 0.67608 | 48115.1578 | 0.54226 | 0.91965 | 0.0028921 | 0.40721 | 1.058e-06 | 0.36152 | 40909.5107 | 0.73098 | 0.95253 | 0.025013 |  | 0.035913
0.5896 | 7.5488e-07 | 0.55596 | 18000.3166 | 0.20756 | 0.8221 | 0.01735 |  | 0.055681 | 1.0848e-08 | 0.93868 | 59799.9736 | 0.040681 | 0.82332 | 0.00043495 | 0.45405 | 1.1275e-06 | 0.43338 | 42465.3387 | 0.3862 | 0.91786 | 0.030087 |  | 0.047871
0.046426 | 1.2969e-07 | 0.7312 | 19797.1235 | 0.6602 | 0.89308 | 0.0023612 |  | 0.076186 | 1.3626e-08 | 0.6811 | 48250.2937 | 0.14834 | 0.86461 | 0.00044584 | 0.63641 | 1.4274e-06 | 0.93628 | 59566.95 | 0.2904 | 0.90551 | 0.05031 |  | 0.053117
0.26053 | 3.7668e-07 | 0.01476 | 11324.2904 | 0.982 | 0.95715 | 0.0034555 |  | 0.30003 | 4.0633e-08 | 0.36171 | 40913.7124 | 0.84538 | 0.95146 | 0.00096366 | 0.91922 | 2.2893e-06 | 0.19988 | 37108.0479 | 0.031212 | 0.82907 | 0.069494 |  | 0.073913
0.72601 | 9.7646e-07 | 0.05896 | 12801.1062 | 0.85428 | 0.92201 | 0.012433 |  | 0.93453 | 2.0579e-07 | 0.21612 | 37531.2459 | 0.77321 | 0.94318 | 0.0046667 | 0.41642 | 1.0715e-06 | 0.50973 | 44129.2028 | 0.38718 | 0.91797 | 0.029403 |  | 0.046503
0.76327 | 1.053e-06 | 0.28117 | 15585.9681 | 0.72346 | 0.90177 | 0.01646 |  | 0.59499 | 8.3175e-08 | 0.98764 | 68811.5911 | 0.68539 | 0.93406 | 0.0031534 | 0.86985 | 2.0389e-06 | 0.51061 | 44148.8051 | 0.032475 | 0.83025 | 0.067686 |  | 0.087299
0.73201 | 9.8816e-07 | 0.87717 | 22074.8269 | 0.11817 | 0.79699 | 0.026265 |  | 0.31509 | 4.2483e-08 | 0.27812 | 39038.9316 | 0.99623 | 0.98517 | 0.00087213 | 0.39961 | 1.0468e-06 | 0.82038 | 52752.318 | 0.034134 | 0.83175 | 0.038395 |  | 0.065532
0.48781 | 6.2395e-07 | 0.6452 | 18853.9401 | 0.96581 | 0.94925 | 0.0083571 |  | 0.41794 | 5.5758e-08 | 0.72793 | 49578.6374 | 0.92945 | 0.96359 | 0.0015097 | 0.23778 | 8.0829e-07 | 0.80958 | 52327.1096 | 0.9434 | 0.97699 | 0.022291 |  | 0.032157
0.48357 | 6.1889e-07 | 0.84317 | 21407.9405 | 0.8224 | 0.9166 | 0.010594 |  | 0.16557 | 2.4619e-08 | 0.48208 | 43521.5717 | 0.47947 | 0.91309 | 0.00067661 | 0.31213 | 9.192e-07 | 0.143 | 35475.8729 | 0.57185 | 0.93738 | 0.020326 |  | 0.031597
0.14112 | 2.5013e-07 | 0.6011 | 18420.8193 | 0.43368 | 0.86205 | 0.0050086 |  | 0.8899 | 1.7213e-07 | 0.0028917 | 25286.7801 | 0.88655 | 0.95686 | 0.0027329 | 0.054754 | 4.5958e-07 | 0.48263 | 43533.5917 | 0.95944 | 0.97992 | 0.010611 |  | 0.018353
0.011301 | 6.0289e-08 | 0.86478 | 21816.2442 | 0.14059 | 0.8044 | 0.001562 |  | 0.51676 | 7.01e-08 | 0.86609 | 54809.6472 | 0.22275 | 0.87957 | 0.0024293 | 0.57215 | 1.314e-06 | 0.27101 | 38872.6148 | 0.62804 | 0.94276 | 0.030667 |  | 0.034659
0.024109 | 9.0368e-08 | 0.030935 | 12046.7962 | 0.4688 | 0.86709 | 0.0015241 |  | 0.45943 | 6.1544e-08 | 0.32342 | 40069.5149 | 0.99074 | 0.98079 | 0.0013129 | 0.81008 | 1.8286e-06 | 0.07415 | 32888.812 | 0.4707 | 0.92722 | 0.03954 |  | 0.042377
0.92561 | 1.6203e-06 | 0.017135 | 11460.0783 | 0.36444 | 0.85152 | 0.028981 |  | 0.26328 | 3.6191e-08 | 0.18209 | 36626.1197 | 0.79577 | 0.94566 | 0.00079903 | 0.49907 | 1.1962e-06 | 0.24672 | 38293.3632 | 0.45394 | 0.92544 | 0.029009 |  | 0.058789
0.008302 | 5.1272e-08 | 0.26384 | 15424.1406 | 0.80307 | 0.91351 | 0.00074968 |  | 0.095409 | 1.61e-08 | 0.16343 | 36095.0331 | 0.1711 | 0.86971 | 0.00043645 | 0.19216 | 7.3645e-07 | 0.29028 | 39319.8315 | 0.25086 | 0.89955 | 0.019504 |  | 0.02069
0.63689 | 8.2393e-07 | 0.91397 | 22997.164 | 0.30358 | 0.84132 | 0.019424 |  | 0.024111 | 6.0052e-09 | 0.62332 | 46762.6987 | 0.033239 | 0.81746 | 0.00021081 | 0.70112 | 1.5556e-06 | 0.20631 | 37277.4055 | 0.78189 | 0.95752 | 0.033552 |  | 0.053187
0.88959 | 1.4326e-06 | 0.16947 | 14454.3272 | 0.77164 | 0.90872 | 0.020864 |  | 0.29782 | 4.0363e-08 | 0.66177 | 47736.8764 | 0.60002 | 0.9255 | 0.0011551 | 0.54219 | 1.2646e-06 | 0.3575 | 40821.7817 | 0.11425 | 0.87051 | 0.036814 |  | 0.058833
0.41223 | 5.3721e-07 | 0.010995 | 11068.9006 | 0.12869 | 0.8006 | 0.011764 |  | 0.44052 | 5.887e-08 | 0.51582 | 44264.194 | 0.6898 | 0.9345 | 0.0015553 | 0.91742 | 2.278e-06 | 0.36692 | 41027.447 | 0.14915 | 0.8799 | 0.065086 |  | 0.078406
0.28851 | 4.0564e-07 | 0.70055 | 19442.1572 | 0.70327 | 0.89896 | 0.0071352 |  | 0.047184 | 9.6337e-09 | 0.006189 | 26629.211 | 0.81325 | 0.94764 | 0.00016574 | 0.80779 | 1.8217e-06 | 0.48795 | 43650.0784 | 0.41056 | 0.92067 | 0.049265 |  | 0.056566
0.85717 | 1.3074e-06 | 0.23616 | 15157.652 | 0.9558 | 0.94555 | 0.015605 |  | 0.57699 | 7.9994e-08 | 0.99528 | 73797.9706 | 0.95895 | 0.96963 | 0.0030749 | 0.037508 | 4.0502e-07 | 0.31001 | 39768.8106 | 0.57871 | 0.93804 | 0.0097529 |  | 0.028433
0.4263 | 5.5287e-07 | 0.33345 | 16057.3261 | 0.29094 | 0.83905 | 0.01152 |  | 0.58931 | 8.2158e-08 | 0.73772 | 49874.5561 | 0.15978 | 0.86725 | 0.0027322 | 0.3345 | 9.5187e-07 | 0.7734 | 51022.1664 | 0.43214 | 0.92308 | 0.028829 |  | 0.043081
0.8983 | 1.4721e-06 | 0.11931 | 13826.0656 | 0.48976 | 0.87003 | 0.025613 |  | 0.69981 | 1.0455e-07 | 0.75061 | 50275.9381 | 0.45969 | 0.91095 | 0.0032096 | 0.20099 | 7.5071e-07 | 0.23546 | 38017.6471 | 0.54554 | 0.93481 | 0.017627 |  | 0.04645
0.15302 | 2.633e-07 | 0.90283 | 22687.5986 | 0.83844 | 0.91926 | 0.004608 |  | 0.63828 | 9.1341e-08 | 0.46149 | 43073.446 | 0.85078 | 0.95213 | 0.0022561 | 0.60738 | 1.3748e-06 | 0.58783 | 45907.8283 | 0.54215 | 0.93448 | 0.03738 |  | 0.044244
0.081887 | 1.7967e-07 | 0.75568 | 20100.4444 | 0.70975 | 0.89986 | 0.0032011 |  | 0.59471 | 8.3124e-08 | 0.41966 | 42169.1955 | 0.41777 | 0.90628 | 0.0022708 | 0.67409 | 1.4999e-06 | 0.46504 | 43150.555 | 0.10124 | 0.86637 | 0.045595 |  | 0.051067
0.99371 | 2.7281e-06 | 0.20015 | 14791.1271 | 0.9607 | 0.94729 | 0.031709 |  | 0.060085 | 1.1461e-08 | 0.56514 | 45378.8822 | 0.58995 | 0.92448 | 0.00031621 | 0.53472 | 1.2525e-06 | 0.21805 | 37580.4306 | 0.41396 | 0.92105 | 0.03034 |  | 0.062365
0.97147 | 2.0607e-06 | 0.064559 | 12919.3608 | 0.44004 | 0.86298 | 0.036223 |  | 0.18929 | 2.7423e-08 | 0.1923 | 36905.3894 | 0.87735 | 0.95559 | 0.00059024 | 0.21197 | 7.6816e-07 | 0.13923 | 35356.7555 | 0.6444 | 0.94431 | 0.016571 |  | 0.053384
0.98572 | 2.3694e-06 | 0.43014 | 16895.3672 | 0.18693 | 0.81717 | 0.054303 |  | 0.15593 | 2.3474e-08 | 0.22479 | 37751.3145 | 0.62658 | 0.92816 | 0.00055898 | 0.43748 | 1.1027e-06 | 0.3659 | 41005.0883 | 0.13487 | 0.87631 | 0.031761 |  | 0.086623
0.60289 | 7.7365e-07 | 0.37758 | 16442.6534 | 0.038441 | 0.75412 | 0.02146 |  | 0.801 | 1.3281e-07 | 0.58407 | 45819.3262 | 0.88157 | 0.95616 | 0.0034191 | 0.76452 | 1.7026e-06 | 0.47455 | 43357.3133 | 0.53699 | 0.93397 | 0.044321 |  | 0.0692
0.3068 | 4.2463e-07 | 0.090399 | 13391.0261 | 0.33816 | 0.84725 | 0.0080909 |  | 0.14887 | 2.2632e-08 | 0.83466 | 53345.5106 | 0.95654 | 0.96906 | 0.00064632 | 0.77188 | 1.7215e-06 | 0.46466 | 43142.2259 | 0.6836 | 0.94802 | 0.043045 |  | 0.051782
0.70021 | 9.2854e-07 | 0.19944 | 14783.6029 | 0.98796 | 0.9613 | 0.0097461 |  | 0.41568 | 5.5451e-08 | 0.40667 | 41888.9179 | 0.4702 | 0.91209 | 0.0014863 | 0.49779 | 1.1942e-06 | 0.77661 | 51131.7856 | 0.89074 | 0.96946 | 0.032794 |  | 0.044027
0.69295 | 9.1568e-07 | 0.090341 | 13390.0741 | 0.0099872 | 0.71018 | 0.027601 |  | 0.27222 | 3.7263e-08 | 0.83941 | 53552.0289 | 0.73752 | 0.9394 | 0.0011351 | 0.069258 | 4.985e-07 | 0.83985 | 53571.4187 | 0.22081 | 0.89453 | 0.01655 |  | 0.045286
0.55041 | 7.0204e-07 | 0.42105 | 16817.232 | 0.99192 | 0.96493 | 0.0078529 |  | 0.066747 | 1.237e-08 | 0.7282 | 49586.6563 | 0.54599 | 0.92003 | 0.00036881 | 0.87192 | 2.0475e-06 | 0.69887 | 48738.7194 | 0.9562 | 0.97928 | 0.05258 |  | 0.060801
0.75305 | 1.031e-06 | 0.49194 | 17430.2216 | 0.50316 | 0.87189 | 0.019404 |  | 0.69305 | 1.0299e-07 | 0.85117 | 54083.938 | 0.87 | 0.9546 | 0.0030681 | 0.0083078 | 2.5417e-07 | 0.28011 | 39085.1702 | 0.89 | 0.96937 | 0.0054969 |  | 0.027969
0.073706 | 1.6893e-07 | 0.34223 | 16134.6163 | 0.41821 | 0.85977 | 0.0032467 |  | 0.016851 | 4.6864e-09 | 0.010517 | 27681.6062 | 0.8659 | 0.95406 | 8.0743e-05 | 0.25388 | 8.3279e-07 | 0.14522 | 35545.3457 | 0.042886 | 0.83869 | 0.024181 |  | 0.027509
0.1372 | 2.4574e-07 | 0.61147 | 18520.4676 | 0.65475 | 0.89234 | 0.0043481 |  | 0.14846 | 2.2583e-08 | 0.80709 | 52231.5954 | 0.67235 | 0.93274 | 0.00068316 | 0.67245 | 1.4967e-06 | 0.38644 | 41451.5404 | 0.83814 | 0.96336 | 0.034687 |  | 0.039718
0.62244 | 8.0213e-07 | 0.2493 | 15285.5631 | 0.13639 | 0.80309 | 0.01876 |  | 0.49014 | 6.6037e-08 | 0.47828 | 43438.7078 | 0.98981 | 0.98024 | 0.0015202 | 0.11982 | 6.0915e-07 | 0.60896 | 46412.4474 | 0.96134 | 0.9803 | 0.014909 |  | 0.035189
0.74362 | 1.0114e-06 | 0.17365 | 14501.8328 | 0.22512 | 0.82602 | 0.021473 |  | 0.73155 | 1.1233e-07 | 0.53653 | 44727.2701 | 0.592 | 0.92469 | 0.003064 | 0.12202 | 6.1341e-07 | 0.85119 | 54084.8768 | 0.43175 | 0.92303 | 0.019447 |  | 0.043984
0.81172 | 1.1699e-06 | 0.13323 | 14013.0812 | 0.05431 | 0.76655 | 0.030209 |  | 0.82735 | 1.4236e-07 | 0.69246 | 48560.4993 | 0.67741 | 0.93325 | 0.0040583 | 0.54657 | 1.2717e-06 | 0.32504 | 40105.4382 | 0.27518 | 0.90329 | 0.033809 |  | 0.068076
0.29174 | 4.0898e-07 | 0.26254 | 15411.9083 | 0.75051 | 0.90563 | 0.0062353 |  | 0.82277 | 1.4061e-07 | 0.87634 | 55346.9924 | 0.5855 | 0.92404 | 0.0045312 | 0.16215 | 6.863e-07 | 0.8463 | 53859.9235 | 0.19305 | 0.8894 | 0.023087 |  | 0.033854
0.7279 | 9.8013e-07 | 0.020901 | 11648.1722 | 0.043679 | 0.75865 | 0.025053 |  | 0.81088 | 1.3624e-07 | 0.01719 | 28764.0226 | 0.75064 | 0.94077 | 0.0025502 | 0.1573 | 6.7791e-07 | 0.44699 | 42759.4238 | 0.80351 | 0.95971 | 0.016302 |  | 0.043905
0.7349 | 9.9386e-07 | 0.7784 | 20401.4099 | 0.34764 | 0.84881 | 0.021768 |  | 0.049417 | 9.9574e-09 | 0.36211 | 40922.477 | 0.53466 | 0.91887 | 0.00025798 | 0.44001 | 1.1065e-06 | 0.38709 | 41465.5078 | 0.2338 | 0.89677 | 0.030579 |  | 0.052605
0.46029 | 5.9157e-07 | 0.40253 | 16657.8757 | 0.072396 | 0.77736 | 0.015368 |  | 0.82316 | 1.4075e-07 | 0.40479 | 41848.2276 | 0.53823 | 0.91924 | 0.0037031 | 0.8932 | 2.1444e-06 | 0.15034 | 35703.4263 | 0.60153 | 0.94023 | 0.047221 |  | 0.066292
0.58751 | 7.5197e-07 | 0.85768 | 21676.5891 | 0.12978 | 0.80096 | 0.019639 |  | 0.32461 | 4.3662e-08 | 0.065773 | 32480.4563 | 0.69604 | 0.93514 | 0.00091117 | 0.40533 | 1.0552e-06 | 0.88839 | 56027.7801 | 0.53606 | 0.93387 | 0.033718 |  | 0.054269
0.050854 | 1.3652e-07 | 0.078469 | 13185.9939 | 0.19278 | 0.81861 | 0.0029061 |  | 0.71683 | 1.0862e-07 | 0.22339 | 37716.0251 | 0.95147 | 0.96792 | 0.002288 | 0.88386 | 2.1e-06 | 0.71037 | 49064.5846 | 0.87087 | 0.96705 | 0.055882 |  | 0.061076
0.34824 | 4.6809e-07 | 0.5836 | 18255.5119 | 0.92831 | 0.93748 | 0.0065692 |  | 0.53545 | 7.3058e-08 | 0.086833 | 33452.9798 | 0.28262 | 0.88903 | 0.0017966 | 0.41335 | 1.067e-06 | 0.40015 | 41748.1369 | 0.38302 | 0.91748 | 0.028148 |  | 0.036514
0.91704 | 1.5689e-06 | 0.22605 | 15057.3199 | 0.29655 | 0.84006 | 0.031904 |  | 0.069586 | 1.2751e-08 | 0.96174 | 62582.5977 | 0.11574 | 0.85606 | 0.00050235 | 0.63908 | 1.4323e-06 | 0.066836 | 32534.0968 | 0.55915 | 0.93614 | 0.029824 |  | 0.062231
0.8451 | 1.2674e-06 | 0.16136 | 14360.3143 | 0.18701 | 0.8172 | 0.027732 |  | 0.59244 | 8.2716e-08 | 0.90766 | 57256.2827 | 0.82303 | 0.94877 | 0.0026179 | 0.47761 | 1.1632e-06 | 0.36404 | 40964.5789 | 0.93141 | 0.97506 | 0.025771 |  | 0.056122
0.26418 | 3.8046e-07 | 0.12818 | 13946.6786 | 0.82299 | 0.91669 | 0.0052086 |  | 0.26937 | 3.692e-08 | 0.68023 | 48226.6639 | 0.35596 | 0.8989 | 0.0011272 | 0.72674 | 1.6119e-06 | 0.20895 | 37346.2445 | 0.28163 | 0.90424 | 0.040738 |  | 0.047074
0.5703 | 7.2842e-07 | 0.41448 | 16760.7225 | 0.15328 | 0.80819 | 0.017173 |  | 0.27302 | 3.736e-08 | 0.12957 | 35042.5707 | 0.21315 | 0.87788 | 0.00097432 | 0.78091 | 1.7455e-06 | 0.35773 | 40826.7514 | 0.41282 | 0.92092 | 0.044904 |  | 0.063052
0.9814 | 2.2523e-06 | 0.14488 | 14161.3114 | 0.09864 | 0.78956 | 0.054113 |  | 0.71028 | 1.0703e-07 | 0.63951 | 47166.1128 | 0.17088 | 0.86967 | 0.0034171 | 0.70831 | 1.571e-06 | 0.82882 | 53098.5576 | 0.51254 | 0.93152 | 0.048278 |  | 0.10581
0.93764 | 1.7029e-06 | 0.76241 | 20187.407 | 0.16517 | 0.81152 | 0.042064 |  | 0.61891 | 8.7589e-08 | 0.20722 | 37301.1607 | 0.029446 | 0.814 | 0.0027569 | 0.0023506 | 1.77e-07 | 0.032753 | 30383.1072 | 0.25399 | 0.90005 | 0.0039699 |  | 0.048791
0.69411 | 9.1772e-07 | 0.37146 | 16389.6316 | 0.89688 | 0.93021 | 0.012606 |  | 0.84769 | 1.5072e-07 | 0.086194 | 33425.8676 | 0.76953 | 0.94278 | 0.0031304 | 0.29107 | 8.8825e-07 | 0.47488 | 43364.4892 | 0.5733 | 0.93752 | 0.022918 |  | 0.038654
0.92946 | 1.6452e-06 | 0.98364 | 26825.7027 | 0.93457 | 0.93913 | 0.029497 |  | 0.033767 | 7.6005e-09 | 0.3283 | 40178.2163 | 0.56321 | 0.92179 | 0.00019282 | 0.91026 | 2.2353e-06 | 0.68645 | 48395.4753 | 0.39999 | 0.91946 | 0.065502 |  | 0.095192
0.52827 | 6.7363e-07 | 0.13621 | 14051.655 | 0.43173 | 0.86177 | 0.012236 |  | 0.35922 | 4.8023e-08 | 0.18284 | 36646.6716 | 0.21327 | 0.8779 | 0.0012861 | 0.6238 | 1.4042e-06 | 0.94137 | 60070.3755 | 0.56669 | 0.93688 | 0.047278 |  | 0.0608
0.49303 | 6.3022e-07 | 0.34354 | 16146.1051 | 0.045794 | 0.76034 | 0.017099 |  | 0.82675 | 1.4213e-07 | 0.35537 | 40775.1326 | 0.80748 | 0.94698 | 0.0034042 | 0.83944 | 1.9236e-06 | 0.25892 | 38586.8228 | 0.10814 | 0.86862 | 0.054376 |  | 0.07488
0.39769 | 5.2122e-07 | 0.39321 | 16577.5865 | 0.56654 | 0.88051 | 0.0092598 |  | 0.86354 | 1.5801e-07 | 0.66027 | 47697.8729 | 0.57502 | 0.92298 | 0.0045442 | 0.29035 | 8.872e-07 | 0.49108 | 43718.6218 | 0.77678 | 0.95701 | 0.021901 |  | 0.035705
0.17501 | 2.8716e-07 | 0.7914 | 20583.825 | 0.92439 | 0.93649 | 0.0043655 |  | 0.37565 | 5.0141e-08 | 0.32289 | 40057.5744 | 0.19451 | 0.87443 | 0.0014297 | 0.52968 | 1.2444e-06 | 0.29686 | 39470.5409 | 0.017713 | 0.81257 | 0.040389 |  | 0.046184
0.070872 | 1.6512e-07 | 0.59325 | 18346.3053 | 0.60012 | 0.88501 | 0.0030037 |  | 0.34341 | 4.6015e-08 | 0.99368 | 72308.9636 | 0.02935 | 0.81391 | 0.0021042 | 0.794 | 1.7816e-06 | 0.037862 | 30785.2136 | 0.58033 | 0.9382 | 0.035374 |  | 0.040482
0.42119 | 5.4715e-07 | 0.92916 | 23480.2623 | 0.7634 | 0.9075 | 0.010263 |  | 0.037007 | 8.1075e-09 | 0.69351 | 48589.5875 | 0.070668 | 0.84004 | 0.00027907 | 0.93185 | 2.3755e-06 | 0.45292 | 42887.8049 | 0.60386 | 0.94046 | 0.060297 |  | 0.070839
0.8309 | 1.2238e-06 | 0.61066 | 18512.6242 | 0.7172 | 0.9009 | 0.02083 |  | 0.87442 | 1.6349e-07 | 0.3223 | 40044.492 | 0.046386 | 0.82719 | 0.0051826 | 0.72016 | 1.5971e-06 | 0.73629 | 49830.7722 | 0.29445 | 0.90608 | 0.049194 |  | 0.075206
0.7613 | 1.0487e-06 | 0.45782 | 17133.8945 | 0.70213 | 0.8988 | 0.017371 |  | 0.82082 | 1.3987e-07 | 0.61933 | 46664.6969 | 0.57136 | 0.92261 | 0.0039592 | 0.30142 | 9.035e-07 | 0.11909 | 34685.8126 | 0.012848 | 0.80353 | 0.02814 |  | 0.04947
0.052061 | 1.3835e-07 | 0.38546 | 16510.6967 | 0.34481 | 0.84835 | 0.0028068 |  | 0.39517 | 5.2702e-08 | 0.27309 | 38921.5057 | 0.36403 | 0.89991 | 0.0013851 | 0.35639 | 9.8375e-07 | 0.97335 | 64633.0093 | 0.065298 | 0.8519 | 0.039846 |  | 0.044038
0.32809 | 4.4687e-07 | 0.23588 | 15154.8256 | 0.72985 | 0.90267 | 0.0068664 |  | 0.21486 | 3.0439e-08 | 0.37392 | 41179.8447 | 0.47384 | 0.91249 | 0.00080525 | 0.88508 | 2.1056e-06 | 0.6364 | 47087.8135 | 0.8881 | 0.96913 | 0.053738 |  | 0.06141
0.072115 | 1.6679e-07 | 0.42314 | 16835.1859 | 0.93498 | 0.93924 | 0.0022065 |  | 0.15922 | 2.3865e-08 | 0.36232 | 40927.1695 | 0.50894 | 0.91621 | 0.00062263 | 0.20925 | 7.6387e-07 | 0.49279 | 43756.144 | 0.10873 | 0.8688 | 0.023298 |  | 0.026128
0.46949 | 6.0228e-07 | 0.54455 | 17896.8398 | 0.50723 | 0.87245 | 0.011431 |  | 0.44682 | 5.9753e-08 | 0.28102 | 39106.2662 | 0.50337 | 0.91562 | 0.0015115 | 0.35914 | 9.8775e-07 | 0.1381 | 35320.6963 | 0.76573 | 0.95591 | 0.02049 |  | 0.033433
0.17411 | 2.8619e-07 | 0.037387 | 12254.2638 | 0.93355 | 0.93885 | 0.0031793 |  | 0.86105 | 1.5681e-07 | 0.69102 | 48520.7246 | 0.97557 | 0.97425 | 0.0040601 | 0.99334 | 3.4556e-06 | 0.97818 | 65741.843 | 0.37952 | 0.91707 | 0.12927 |  | 0.13651
0.09588 | 1.9732e-07 | 0.20322 | 14823.4635 | 0.34726 | 0.84875 | 0.0038556 |  | 0.27675 | 3.7809e-08 | 0.86743 | 54877.8643 | 0.32977 | 0.89555 | 0.001275 | 0.75429 | 1.677e-06 | 0.19272 | 36916.7302 | 0.1729 | 0.88528 | 0.044255 |  | 0.049386
0.11448 | 2.1966e-07 | 0.46359 | 17183.7422 | 0.69612 | 0.89797 | 0.003658 |  | 0.31346 | 4.2282e-08 | 0.1941 | 36953.863 | 0.64798 | 0.9303 | 0.00098495 | 0.017724 | 3.1929e-07 | 0.42384 | 42259.4652 | 0.66098 | 0.94588 | 0.0078951 |  | 0.012538
0.1203 | 2.2646e-07 | 0.17551 | 14522.8432 | 0.35303 | 0.84969 | 0.0043791 |  | 0.076154 | 1.3622e-08 | 0.18297 | 36650.3012 | 0.18212 | 0.87199 | 0.00037042 | 0.63044 | 1.4163e-06 | 0.33291 | 40280.4659 | 0.36165 | 0.91491 | 0.036656 |  | 0.041405
0.66358 | 8.6606e-07 | 0.79069 | 20573.5693 | 0.62233 | 0.88799 | 0.016409 |  | 0.084027 | 1.4647e-08 | 0.10431 | 34150.2794 | 0.88451 | 0.95657 | 0.00029496 | 0.34281 | 9.6397e-07 | 0.47024 | 43263.5251 | 0.18093 | 0.88697 | 0.02804 |  | 0.044745
0.91396 | 1.5517e-06 | 0.76373 | 20204.6659 | 0.67071 | 0.8945 | 0.028362 |  | 0.7936 | 1.3033e-07 | 0.13349 | 35171.4712 | 0.97294 | 0.97342 | 0.0025346 | 0.86393 | 2.0148e-06 | 0.20833 | 37330.0681 | 0.76433 | 0.95578 | 0.043748 |  | 0.074645
0.55296 | 7.0538e-07 | 0.75438 | 20083.7806 | 0.78938 | 0.91139 | 0.011931 |  | 0.26268 | 3.6118e-08 | 0.69915 | 48746.6078 | 0.17796 | 0.87115 | 0.0011746 | 0.43611 | 1.1007e-06 | 0.67295 | 48031.6898 | 0.96939 | 0.98205 | 0.027691 |  | 0.040796
0.8574 | 1.3082e-06 | 0.085638 | 13311.4058 | 0.53296 | 0.87597 | 0.02184 |  | 0.70135 | 1.0491e-07 | 0.0061887 | 26629.1067 | 0.84624 | 0.95156 | 0.0017743 | 0.36399 | 9.9481e-07 | 0.41185 | 42000.782 | 0.21476 | 0.89346 | 0.02795 |  | 0.051564
0.092774 | 1.9347e-07 | 0.65066 | 18909.5091 | 0.58111 | 0.88247 | 0.0036062 |  | 0.89864 | 1.7753e-07 | 0.26331 | 38691.1527 | 0.92034 | 0.96202 | 0.0038946 | 0.78842 | 1.766e-06 | 0.81129 | 52393.0674 | 0.82838 | 0.96231 | 0.05035 |  | 0.057851
0.65387 | 8.5045e-07 | 0.87989 | 22134.2743 | 0.37218 | 0.85275 | 0.018996 |  | 0.30611 | 4.1377e-08 | 0.59908 | 46175.0219 | 0.14074 | 0.86277 | 0.0013216 | 0.65952 | 1.4712e-06 | 0.75687 | 50475.9327 | 0.27977 | 0.90397 | 0.045941 |  | 0.066259
0.17887 | 2.913e-07 | 0.73863 | 19887.032 | 0.73568 | 0.9035 | 0.0050794 |  | 0.71515 | 1.0821e-07 | 0.65966 | 47681.9783 | 0.18926 | 0.87341 | 0.0034533 | 0.50382 | 1.2036e-06 | 0.94981 | 60998.9734 | 0.87551 | 0.9676 | 0.038936 |  | 0.047469
0.1469 | 2.5656e-07 | 0.30069 | 15764.5255 | 0.48949 | 0.87 | 0.0046811 |  | 0.40299 | 5.3743e-08 | 0.21323 | 37457.0014 | 0.61227 | 0.92672 | 0.0012778 | 0.45272 | 1.1255e-06 | 0.80138 | 52016.2638 | 0.69549 | 0.94914 | 0.032798 |  | 0.038757
0.87182 | 1.3603e-06 | 0.15994 | 14343.607 | 0.81988 | 0.91618 | 0.018926 |  | 0.19375 | 2.7949e-08 | 0.67171 | 47998.7016 | 0.61471 | 0.92697 | 0.00080058 | 0.043621 | 4.2572e-07 | 0.40435 | 41838.8251 | 0.32286 | 0.90997 | 0.011461 |  | 0.031188
0.035233 | 1.1121e-07 | 0.47603 | 17291.6371 | 0.62581 | 0.88845 | 0.001941 |  | 0.85223 | 1.5274e-07 | 0.13078 | 35082.547 | 0.75767 | 0.94152 | 0.003305 | 0.59274 | 1.3492e-06 | 0.28881 | 39286.1826 | 0.6381 | 0.94371 | 0.031662 |  | 0.036908
0.26412 | 3.8039e-07 | 0.24893 | 15281.9741 | 0.61828 | 0.88744 | 0.00633 |  | 0.56477 | 7.7897e-08 | 0.069082 | 32645.6608 | 0.33407 | 0.89611 | 0.0018483 | 0.48379 | 1.1726e-06 | 0.86386 | 54697.0595 | 0.74541 | 0.95393 | 0.035325 |  | 0.043503
0.34403 | 4.6364e-07 | 0.91903 | 23149.1454 | 0.46785 | 0.86696 | 0.010056 |  | 0.98055 | 2.8249e-07 | 0.75535 | 50427.0894 | 0.40102 | 0.90435 | 0.0088083 | 0.38372 | 1.0236e-06 | 0.52911 | 44560.7101 | 0.98053 | 0.98494 | 0.023813 |  | 0.042677
0.97663 | 2.1503e-06 | 0.93496 | 23688.8033 | 0.13949 | 0.80406 | 0.057388 |  | 0.024849 | 6.1326e-09 | 0.79777 | 51882.4058 | 0.1494 | 0.86486 | 0.00021018 | 0.87482 | 2.0599e-06 | 0.42 | 42176.55 | 0.88207 | 0.96839 | 0.04777 |  | 0.10537
0.59664 | 7.6476e-07 | 0.8576 | 21675.0538 | 0.67162 | 0.89462 | 0.014474 |  | 0.58461 | 8.1327e-08 | 0.25255 | 38434.3032 | 0.19395 | 0.87432 | 0.0022618 | 0.10807 | 5.8579e-07 | 0.35149 | 40690.0065 | 0.85837 | 0.96561 | 0.013273 |  | 0.030009
0.47433 | 6.0796e-07 | 0.72753 | 19753.2238 | 0.16004 | 0.8101 | 0.014978 |  | 0.24675 | 3.4217e-08 | 0.56772 | 45438.5592 | 0.16851 | 0.86916 | 0.0010679 | 0.54057 | 1.262e-06 | 0.85448 | 54239.5093 | 0.2329 | 0.89661 | 0.042115 |  | 0.058161
0.076194 | 1.7223e-07 | 0.62517 | 18654.0662 | 0.40741 | 0.85816 | 0.0035186 |  | 0.040921 | 8.7052e-09 | 0.4591 | 43021.6867 | 0.44241 | 0.90905 | 0.00023958 | 0.83384 | 1.9044e-06 | 0.49397 | 43782.0221 | 0.34131 | 0.91237 | 0.052657 |  | 0.056415
0.056612 | 1.4509e-07 | 0.082384 | 13255.3534 | 0.46484 | 0.86653 | 0.0025297 |  | 0.4035 | 5.3811e-08 | 0.77245 | 50989.9903 | 0.82644 | 0.94917 | 0.0015418 | 0.46618 | 1.1458e-06 | 0.30761 | 39714.6474 | 0.32463 | 0.9102 | 0.029723 |  | 0.033794
0.10922 | 2.1346e-07 | 0.64811 | 18883.4979 | 0.57328 | 0.88142 | 0.0039938 |  | 0.84389 | 1.4909e-07 | 0.85135 | 54092.4105 | 0.81141 | 0.94743 | 0.0045069 | 0.43945 | 1.1057e-06 | 0.4291 | 42372.926 | 0.81649 | 0.96105 | 0.026285 |  | 0.034786
0.63157 | 8.1582e-07 | 0.14038 | 14104.9086 | 0.50257 | 0.87181 | 0.014177 |  | 0.4766 | 6.4031e-08 | 0.65976 | 47684.4426 | 0.96782 | 0.97192 | 0.0016413 | 0.47827 | 1.1642e-06 | 0.45456 | 42923.2884 | 0.88603 | 0.96888 | 0.027382 |  | 0.043201
0.46178 | 5.9329e-07 | 0.48956 | 17409.359 | 0.49654 | 0.87098 | 0.011204 |  | 0.77534 | 1.2457e-07 | 0.72935 | 49621.1235 | 0.82857 | 0.94942 | 0.0034862 | 0.50191 | 1.2006e-06 | 0.56748 | 45432.864 | 0.10002 | 0.86596 | 0.037717 |  | 0.052407
0.61196 | 7.8672e-07 | 0.86068 | 21734.9722 | 0.68294 | 0.89617 | 0.014818 |  | 0.90432 | 1.8128e-07 | 0.24003 | 38130.0331 | 0.82108 | 0.94854 | 0.0040955 | 0.6554 | 1.4633e-06 | 0.08263 | 33272.3294 | 0.8334 | 0.96285 | 0.028201 |  | 0.047114
0.78587 | 1.1046e-06 | 0.3216 | 15952.2725 | 0.97801 | 0.95487 | 0.01278 |  | 0.93065 | 2.0209e-07 | 0.67227 | 48013.6549 | 0.35609 | 0.89892 | 0.0061506 | 0.90554 | 2.2087e-06 | 0.72955 | 49627.0431 | 0.62321 | 0.9423 | 0.062807 |  | 0.081738
0.5493 | 7.0059e-07 | 0.22676 | 15064.4213 | 0.61836 | 0.88745 | 0.01159 |  | 0.21492 | 3.0447e-08 | 0.53994 | 44804.0723 | 0.2427 | 0.88291 | 0.00091452 | 0.51271 | 1.2175e-06 | 0.0033289 | 25522.1133 | 0.58157 | 0.93832 | 0.021158 |  | 0.033662
0.002783 | 2.912e-08 | 0.57734 | 18197.079 | 0.81893 | 0.91603 | 0.0004569 |  | 0.25539 | 3.5247e-08 | 0.4534 | 42898.083 | 0.66353 | 0.93186 | 0.00091491 | 0.82495 | 1.8751e-06 | 0.89703 | 56554.4198 | 0.024067 | 0.8214 | 0.072889 |  | 0.074261
0.75221 | 1.0292e-06 | 0.29073 | 15673.8484 | 0.076527 | 0.7795 | 0.026168 |  | 0.50071 | 6.763e-08 | 0.52371 | 44439.9601 | 0.96394 | 0.97088 | 0.0016315 | 0.24455 | 8.1864e-07 | 0.58934 | 45943.5745 | 0.43448 | 0.92333 | 0.022862 |  | 0.050661
0.012644 | 6.3974e-08 | 0.37622 | 16430.8285 | 0.97055 | 0.95125 | 0.00077316 |  | 0.49911 | 6.7387e-08 | 0.30019 | 39546.4334 | 0.01007 | 0.78499 | 0.0023152 | 0.87387 | 2.0558e-06 | 0.11617 | 34583.5081 | 0.15188 | 0.88055 | 0.052814 |  | 0.055903
0.31118 | 4.292e-07 | 0.057693 | 12773.2988 | 0.77304 | 0.90893 | 0.0059156 |  | 0.79794 | 1.3177e-07 | 0.27871 | 39052.6498 | 0.49706 | 0.91496 | 0.0033359 | 0.039785 | 4.1294e-07 | 0.65707 | 47614.7387 | 0.89811 | 0.9704 | 0.010611 |  | 0.019862
0.57234 | 7.3117e-07 | 0.47794 | 17308.1688 | 0.90903 | 0.93285 | 0.010204 |  | 0.27682 | 3.7817e-08 | 0.34988 | 40654.6689 | 0.77864 | 0.94377 | 0.00091176 | 0.7449 | 1.6542e-06 | 0.53415 | 44673.8539 | 0.3096 | 0.90819 | 0.046861 |  | 0.057976
0.13635 | 2.4478e-07 | 0.10512 | 13621.7625 | 0.56591 | 0.88043 | 0.0040318 |  | 0.94591 | 2.1801e-07 | 0.29291 | 39380.3437 | 0.87421 | 0.95516 | 0.0049564 | 0.40472 | 1.0543e-06 | 0.35411 | 40747.4941 | 0.662 | 0.94597 | 0.02531 |  | 0.034298
0.58938 | 7.5457e-07 | 0.7006 | 19442.6439 | 0.84897 | 0.92108 | 0.011973 |  | 0.45923 | 6.1515e-08 | 0.35529 | 40773.3877 | 0.33281 | 0.89594 | 0.0016843 | 0.92399 | 2.3203e-06 | 0.36936 | 41080.6024 | 0.51659 | 0.93193 | 0.058252 |  | 0.07191
0.78243 | 1.0964e-06 | 0.1536 | 14268.0059 | 0.5579 | 0.87935 | 0.018467 |  | 0.61312 | 8.65e-08 | 0.058261 | 32083.3371 | 0.22359 | 0.87971 | 0.0021322 | 0.12432 | 6.1783e-07 | 0.58953 | 45948.1229 | 0.39671 | 0.91908 | 0.017425 |  | 0.038024
0.39681 | 5.2026e-07 | 0.98714 | 27339.0388 | 0.26617 | 0.8344 | 0.013481 |  | 0.048098 | 9.7666e-09 | 0.1648 | 36135.0878 | 0.19377 | 0.87429 | 0.00026183 | 0.96213 | 2.6633e-06 | 0.10296 | 34099.261 | 0.44168 | 0.92412 | 0.059666 |  | 0.073409
0.92579 | 1.6215e-06 | 0.12743 | 13936.5798 | 0.18138 | 0.81578 | 0.035384 |  | 0.67931 | 9.9901e-08 | 0.79345 | 51724.7385 | 0.087416 | 0.84681 | 0.0035285 | 0.87461 | 2.059e-06 | 0.17242 | 36354.45 | 0.2241 | 0.89511 | 0.05242 |  | 0.091333
0.58519 | 7.4875e-07 | 0.82773 | 21142.6327 | 0.60222 | 0.88529 | 0.014531 |  | 0.7333 | 1.1278e-07 | 0.60437 | 46301.7575 | 0.47085 | 0.91216 | 0.0032495 | 0.47239 | 1.1552e-06 | 0.6999 | 48767.7432 | 0.624 | 0.94237 | 0.032377 |  | 0.050158
0.64919 | 8.4304e-07 | 0.80305 | 20754.3834 | 0.43025 | 0.86155 | 0.017762 |  | 0.09404 | 1.5927e-08 | 0.18658 | 36749.7506 | 0.60285 | 0.92578 | 0.00037448 | 0.20286 | 7.5369e-07 | 0.060582 | 32209.5807 | 0.26645 | 0.90198 | 0.01742 |  | 0.035556
0.47081 | 6.0382e-07 | 0.84327 | 21409.5814 | 0.96831 | 0.95028 | 0.0087723 |  | 0.75629 | 1.19e-07 | 0.97192 | 64341.859 | 0.25557 | 0.88496 | 0.0045872 | 0.16871 | 6.9752e-07 | 0.10436 | 34152.0316 | 0.33732 | 0.91186 | 0.016247 |  | 0.029606
0.91083 | 1.5347e-06 | 0.30322 | 15787.3996 | 0.59694 | 0.88459 | 0.026233 |  | 0.35698 | 4.7737e-08 | 0.39362 | 41606.9567 | 0.29401 | 0.89067 | 0.0013417 | 0.96292 | 2.6734e-06 | 0.87095 | 55059.8901 | 0.2317 | 0.89641 | 0.090235 |  | 0.11781
0.58212 | 7.4452e-07 | 0.28452 | 15616.8411 | 0.33483 | 0.84669 | 0.014921 |  | 0.6413 | 9.1941e-08 | 0.1292 | 35030.203 | 0.74212 | 0.93988 | 0.0019978 | 0.75807 | 1.6863e-06 | 0.24009 | 38131.655 | 0.67705 | 0.9474 | 0.03823 |  | 0.055149
0.89697 | 1.4658e-06 | 0.033018 | 12116.9829 | 0.33622 | 0.84692 | 0.027177 |  | 0.73728 | 1.1382e-07 | 0.08382 | 33324.0324 | 0.32957 | 0.89552 | 0.0027401 | 0.59595 | 1.3547e-06 | 0.56163 | 45298.0752 | 0.7834 | 0.95767 | 0.034408 |  | 0.064325
0.03969 | 1.188e-07 | 0.33709 | 16089.4063 | 0.86221 | 0.92344 | 0.0016794 |  | 0.36227 | 4.8414e-08 | 0.75437 | 50395.5908 | 0.57462 | 0.92294 | 0.0014527 | 0.81656 | 1.8485e-06 | 0.1805 | 36581.8152 | 0.53426 | 0.93369 | 0.042305 |  | 0.045437
0.58942 | 7.5463e-07 | 0.79821 | 20682.6051 | 0.83943 | 0.91943 | 0.012501 |  | 0.44747 | 5.9844e-08 | 0.46384 | 43124.6202 | 0.4304 | 0.90771 | 0.0016551 | 0.25834 | 8.3952e-07 | 0.87747 | 55408.309 | 0.62483 | 0.94245 | 0.026152 |  | 0.040308
0.73998 | 1.004e-06 | 0.4729 | 17264.4058 | 0.3079 | 0.84208 | 0.021188 |  | 0.38251 | 5.1035e-08 | 0.45892 | 43017.7978 | 0.92452 | 0.96273 | 0.0012234 | 0.51908 | 1.2276e-06 | 0.81199 | 52420.4439 | 0.21083 | 0.89275 | 0.040258 |  | 0.062669
0.1098 | 2.1414e-07 | 0.38328 | 16491.9118 | 0.95041 | 0.94377 | 0.0027214 |  | 0.98056 | 2.8252e-07 | 0.34041 | 40446.4318 | 0.42869 | 0.90752 | 0.0074739 | 0.2047 | 7.5663e-07 | 0.74516 | 50104.4267 | 0.14906 | 0.87988 | 0.02464 |  | 0.034836
0.21255 | 3.2686e-07 | 0.47608 | 17292.0363 | 0.70666 | 0.89943 | 0.0054214 |  | 0.17157 | 2.533e-08 | 0.70172 | 48818.9025 | 0.9291 | 0.96353 | 0.00067667 | 0.5538 | 1.2836e-06 | 0.57162 | 45528.7416 | 0.53256 | 0.93353 | 0.034751 |  | 0.040849
0.40798 | 5.3252e-07 | 0.22295 | 15026.1356 | 0.79892 | 0.91286 | 0.0077172 |  | 0.3128 | 4.22e-08 | 0.14346 | 35490.5179 | 0.90804 | 0.96004 | 0.00086666 | 0.4656 | 1.1449e-06 | 0.14562 | 35558.0219 | 0.29188 | 0.90572 | 0.027893 |  | 0.036476
0.86114 | 1.3212e-06 | 0.74635 | 19982.431 | 0.079267 | 0.78087 | 0.035669 |  | 0.50998 | 6.9048e-08 | 0.019716 | 29087.6825 | 0.97415 | 0.9738 | 0.0011364 | 0.57502 | 1.3189e-06 | 0.65125 | 47464.6911 | 0.030529 | 0.82841 | 0.045754 |  | 0.08256
0.25496 | 3.7092e-07 | 0.66366 | 19043.7722 | 0.27825 | 0.8367 | 0.0082611 |  | 0.39678 | 5.2915e-08 | 0.045411 | 31312.8819 | 0.10262 | 0.85204 | 0.0013917 | 0.50767 | 1.2096e-06 | 0.59713 | 46128.3644 | 0.061167 | 0.8498 | 0.039624 |  | 0.049277
0.0021196 | 2.5329e-08 | 0.2773 | 15550.0795 | 0.4437 | 0.8635 | 0.00047292 |  | 0.089898 | 1.54e-08 | 0.57165 | 45529.5018 | 0.86906 | 0.95447 | 0.00039604 | 0.56752 | 1.3063e-06 | 0.52451 | 44457.8662 | 0.81602 | 0.961 | 0.032367 |  | 0.033236
0.53346 | 6.8021e-07 | 0.72641 | 19739.9282 | 0.50293 | 0.87186 | 0.013489 |  | 0.039797 | 8.5351e-09 | 0.47102 | 43280.5201 | 0.70953 | 0.93651 | 0.00022044 | 0.044226 | 4.2767e-07 | 0.2628 | 38678.9425 | 0.49205 | 0.92944 | 0.010331 |  | 0.02404
0.22904 | 3.4405e-07 | 0.98551 | 27085.7124 | 0.064157 | 0.77276 | 0.010449 |  | 0.14492 | 2.216e-08 | 0.16645 | 36182.8822 | 0.11206 | 0.85497 | 0.00062429 | 0.99552 | 3.6281e-06 | 0.41881 | 42150.9918 | 0.95355 | 0.97878 | 0.081586 |  | 0.092659
0.63081 | 8.1468e-07 | 0.19871 | 14775.8551 | 0.026796 | 0.74172 | 0.022897 |  | 0.24507 | 3.4018e-08 | 0.99262 | 71514.5501 | 0.47598 | 0.91272 | 0.0013703 | 0.0065443 | 2.3701e-07 | 0.18054 | 36582.971 | 0.38109 | 0.91725 | 0.0056945 |  | 0.029962
0.43126 | 5.5843e-07 | 0.64861 | 18888.6244 | 0.32767 | 0.84549 | 0.012018 |  | 0.1632 | 2.4338e-08 | 0.85218 | 54131.0639 | 0.89733 | 0.95841 | 0.00072 | 0.1647 | 6.9068e-07 | 0.80138 | 52016.1842 | 0.79162 | 0.9585 | 0.019729 |  | 0.032466
0.79796 | 1.1342e-06 | 0.86184 | 21757.7294 | 0.9447 | 0.942 | 0.017386 |  | 0.96859 | 2.5245e-07 | 0.83592 | 53400.0508 | 0.40005 | 0.90423 | 0.0082129 | 0.038718 | 4.0926e-07 | 0.099302 | 33958.4225 | 0.29255 | 0.90581 | 0.0096712 |  | 0.03527
0.45372 | 5.8398e-07 | 0.73424 | 19833.7172 | 0.83375 | 0.91847 | 0.0094899 |  | 0.080436 | 1.4182e-08 | 0.30677 | 39695.5391 | 0.6336 | 0.92886 | 0.00034984 | 0.1982 | 7.4622e-07 | 0.74811 | 50196.9845 | 0.79951 | 0.9593 | 0.020627 |  | 0.030467
0.18048 | 2.9302e-07 | 0.92323 | 23281.9446 | 0.34533 | 0.84843 | 0.0067845 |  | 0.26025 | 3.5827e-08 | 0.29126 | 39342.3459 | 0.42293 | 0.90687 | 0.00093142 | 0.18765 | 7.2909e-07 | 0.7777 | 51169.1059 | 0.32781 | 0.91062 | 0.022695 |  | 0.030411
0.1674 | 2.7897e-07 | 0.075341 | 13128.952 | 0.367 | 0.85193 | 0.0051787 |  | 0.97674 | 2.7132e-07 | 0.58985 | 45955.6191 | 0.96036 | 0.96998 | 0.0067607 | 0.8503 | 1.9625e-06 | 0.54199 | 44850.4865 | 0.82851 | 0.96232 | 0.048828 |  | 0.060768
0.18202 | 2.9465e-07 | 0.76065 | 20164.5261 | 0.83428 | 0.91856 | 0.0048309 |  | 0.63759 | 9.1204e-08 | 0.29029 | 39320.06 | 0.86234 | 0.9536 | 0.0020806 | 0.26308 | 8.4663e-07 | 0.083808 | 33323.5212 | 0.74283 | 0.95368 | 0.016888 |  | 0.0238
0.66143 | 8.6257e-07 | 0.84838 | 21502.0302 | 0.077264 | 0.77987 | 0.023865 |  | 0.45994 | 6.1616e-08 | 0.86959 | 54989.0325 | 0.22176 | 0.87939 | 0.0021408 | 0.96557 | 2.7089e-06 | 0.63388 | 47024.7427 | 0.80406 | 0.95976 | 0.070677 |  | 0.096683
0.15308 | 2.6338e-07 | 0.81645 | 20960.2903 | 0.69625 | 0.89799 | 0.0048322 |  | 0.23484 | 3.2803e-08 | 0.86027 | 54519.08 | 0.93944 | 0.96545 | 0.00096259 | 0.55744 | 1.2895e-06 | 0.4584 | 43006.444 | 0.5005 | 0.9303 | 0.03367 |  | 0.039465
0.44609 | 5.7524e-07 | 0.17517 | 14519.0502 | 0.6923 | 0.89745 | 0.0089154 |  | 0.73026 | 1.12e-07 | 0.42775 | 42343.93 | 0.073801 | 0.84141 | 0.0035511 | 0.99228 | 3.3909e-06 | 0.57267 | 45553.2462 | 0.12699 | 0.87418 | 0.10489 |  | 0.11736
0.41003 | 5.3478e-07 | 0.10787 | 13662.5247 | 0.90768 | 0.93255 | 0.0065666 |  | 0.76531 | 1.2158e-07 | 0.17347 | 36384.2206 | 0.65943 | 0.93144 | 0.0027904 | 0.13247 | 6.3321e-07 | 0.1354 | 35233.6651 | 0.54246 | 0.93451 | 0.014058 |  | 0.023415
0.47847 | 6.1284e-07 | 0.97399 | 25811.5465 | 0.40153 | 0.85727 | 0.014443 |  | 0.72141 | 1.0976e-07 | 0.57582 | 45626.3844 | 0.51492 | 0.91683 | 0.0030953 | 0.63922 | 1.4326e-06 | 0.98547 | 67949.1304 | 0.44285 | 0.92425 | 0.054492 |  | 0.072029
0.10022 | 2.0263e-07 | 0.16546 | 14408.1272 | 0.36666 | 0.85187 | 0.0038728 |  | 0.65511 | 9.4744e-08 | 0.55127 | 45061.0124 | 0.057091 | 0.83345 | 0.0031614 | 0.90958 | 2.2313e-06 | 0.9959 | 74509.6592 | 0.91139 | 0.97216 | 0.086255 |  | 0.093289
0.89631 | 1.4628e-06 | 0.9404 | 23899.7288 | 0.28942 | 0.83877 | 0.035321 |  | 0.41113 | 5.4836e-08 | 0.9021 | 56881.3595 | 0.89214 | 0.95766 | 0.0016969 | 0.72543 | 1.6089e-06 | 0.66044 | 47702.2881 | 0.55984 | 0.93621 | 0.044917 |  | 0.081935
0.80999 | 1.1653e-06 | 0.65575 | 18961.745 | 0.30404 | 0.8414 | 0.025487 |  | 0.54783 | 7.5071e-08 | 0.25906 | 38590.0832 | 0.80938 | 0.94719 | 0.0017193 | 0.23923 | 8.1052e-07 | 0.94148 | 60081.7675 | 0.55751 | 0.93598 | 0.027335 |  | 0.054541
0.46192 | 5.9346e-07 | 0.010824 | 11055.6766 | 0.38468 | 0.8547 | 0.010358 |  | 0.60798 | 8.5544e-08 | 0.83689 | 53441.8351 | 0.7473 | 0.94042 | 0.0025961 | 0.68486 | 1.5217e-06 | 0.51348 | 44212.3792 | 0.00076892 | 0.73181 | 0.060368 |  | 0.073322
0.043229 | 1.246e-07 | 0.94023 | 23893.0228 | 0.4801 | 0.86868 | 0.0027264 |  | 0.85664 | 1.5474e-07 | 0.093024 | 33709.251 | 0.35187 | 0.89839 | 0.0037205 | 0.68849 | 1.5292e-06 | 0.16182 | 36047.6912 | 0.79587 | 0.95893 | 0.031931 |  | 0.038378
0.30235 | 4.2e-07 | 0.2028 | 14818.9827 | 0.24202 | 0.82959 | 0.0088515 |  | 0.60841 | 8.5623e-08 | 0.54312 | 44876.0137 | 0.23295 | 0.8813 | 0.0025835 | 0.34446 | 9.6638e-07 | 0.39329 | 41599.7584 | 0.99169 | 0.98906 | 0.020807 |  | 0.032242
0.44899 | 5.7855e-07 | 0.55044 | 17950.1428 | 0.4189 | 0.85988 | 0.011567 |  | 0.32044 | 4.3144e-08 | 0.91307 | 57640.7082 | 0.79348 | 0.9454 | 0.0013819 | 0.48132 | 1.1689e-06 | 0.28266 | 39144.2077 | 0.082433 | 0.85949 | 0.03405 |  | 0.046998
0.53252 | 6.7902e-07 | 0.073429 | 13093.3113 | 0.26012 | 0.83323 | 0.013624 |  | 0.64669 | 9.3025e-08 | 0.55141 | 45064.2736 | 0.026624 | 0.81115 | 0.0032391 | 0.041538 | 4.1886e-07 | 0.47466 | 43359.8305 | 0.37873 | 0.91697 | 0.011373 |  | 0.028237
0.090887 | 1.9111e-07 | 0.74989 | 20026.7898 | 0.0023971 | 0.66929 | 0.0068175 |  | 0.79957 | 1.3232e-07 | 0.45816 | 43001.2292 | 0.9604 | 0.96999 | 0.0031075 | 0.85898 | 1.9953e-06 | 0.51013 | 44138.1438 | 0.71879 | 0.95136 | 0.050393 |  | 0.060318
0.50308 | 6.4239e-07 | 0.24131 | 15208.0789 | 0.69134 | 0.89732 | 0.010162 |  | 0.71262 | 1.0759e-07 | 0.5048 | 44020.2213 | 0.4311 | 0.90779 | 0.0030189 | 0.014137 | 2.9795e-07 | 0.054052 | 31845.3071 | 0.50855 | 0.93112 | 0.0062152 |  | 0.019396
0.84767 | 1.2757e-06 | 0.27564 | 15534.6938 | 0.94007 | 0.94066 | 0.015952 |  | 0.5316 | 7.2442e-08 | 0.51306 | 44203.0941 | 0.9572 | 0.96921 | 0.0017472 | 0.23727 | 8.0752e-07 | 0.49448 | 43793.1813 | 0.15305 | 0.88083 | 0.024005 |  | 0.041704
0.77949 | 1.0896e-06 | 0.87629 | 22055.7555 | 0.77221 | 0.9088 | 0.019624 |  | 0.25964 | 3.5755e-08 | 0.82168 | 52804.7011 | 0.83267 | 0.94991 | 0.0010536 | 0.28978 | 8.8636e-07 | 0.50943 | 44122.5846 | 0.41226 | 0.92086 | 0.024151 |  | 0.044829
0.94627 | 1.7719e-06 | 0.95912 | 24787.7147 | 0.68083 | 0.89588 | 0.035835 |  | 0.45864 | 6.1431e-08 | 0.40769 | 41910.8594 | 0.72602 | 0.9382 | 0.0015403 | 0.34649 | 9.6934e-07 | 0.81423 | 52507.9963 | 0.43176 | 0.92304 | 0.030026 |  | 0.067401
0.24673 | 3.6239e-07 | 0.79597 | 20649.8303 | 0.30527 | 0.84162 | 0.008177 |  | 0.31558 | 4.2543e-08 | 0.10676 | 34241.9465 | 0.43776 | 0.90854 | 0.0010026 | 0.91424 | 2.2586e-06 | 0.51363 | 44215.6194 | 0.82466 | 0.96191 | 0.055567 |  | 0.064747
0.17292 | 2.8492e-07 | 0.42869 | 16882.9479 | 0.70008 | 0.89852 | 0.0046939 |  | 0.38483 | 5.134e-08 | 0.043085 | 31157.4769 | 0.73696 | 0.93934 | 0.0010241 | 0.48751 | 1.1784e-06 | 0.47777 | 43427.6357 | 0.70857 | 0.95039 | 0.029438 |  | 0.035156
0.9329 | 1.6686e-06 | 0.72704 | 19747.4318 | 0.90926 | 0.93291 | 0.025178 |  | 0.96177 | 2.4005e-07 | 0.45619 | 42958.6152 | 0.77766 | 0.94366 | 0.0060504 | 0.76366 | 1.7004e-06 | 0.99834 | 79018.7579 | 0.91052 | 0.97204 | 0.069467 |  | 0.1007
0.50184 | 6.4088e-07 | 0.49508 | 17457.6736 | 0.65361 | 0.89219 | 0.011044 |  | 0.59123 | 8.25e-08 | 0.39819 | 41705.7348 | 0.090776 | 0.84803 | 0.0025572 | 0.44157 | 1.1088e-06 | 0.14715 | 35605.4006 | 0.17831 | 0.88642 | 0.02853 |  | 0.042131
0.013146 | 6.5306e-08 | 0.74462 | 19960.8731 | 0.4186 | 0.85983 | 0.0013623 |  | 0.79973 | 1.3237e-07 | 0.058993 | 32123.515 | 0.16377 | 0.86813 | 0.0033749 | 0.41629 | 1.0713e-06 | 0.86066 | 54538.3432 | 0.73774 | 0.95319 | 0.032241 |  | 0.036978
0.083048 | 1.8117e-07 | 0.24628 | 15256.3701 | 0.35325 | 0.84972 | 0.0035592 |  | 0.30364 | 4.1075e-08 | 0.10944 | 34341.2467 | 0.75934 | 0.94169 | 0.00087396 | 0.33029 | 9.4573e-07 | 0.80528 | 52162.71 | 0.74135 | 0.95353 | 0.027369 |  | 0.031803
0.57103 | 7.2941e-07 | 0.21161 | 14910.6716 | 0.79265 | 0.91189 | 0.010589 |  | 0.54689 | 7.4916e-08 | 0.99116 | 70575.3645 | 0.96873 | 0.97218 | 0.0027527 | 0.95635 | 2.5949e-06 | 0.26702 | 38778.8953 | 0.85911 | 0.96569 | 0.056388 |  | 0.069729
0.11739 | 2.2308e-07 | 0.37303 | 16403.1664 | 0.42765 | 0.86117 | 0.0042886 |  | 0.78164 | 1.2651e-07 | 0.65531 | 47569.0676 | 0.30899 | 0.89276 | 0.0038747 | 0.34978 | 9.7412e-07 | 0.086272 | 33429.189 | 0.80609 | 0.95997 | 0.019046 |  | 0.027209
0.22434 | 3.3916e-07 | 0.38559 | 16511.8925 | 0.10323 | 0.79141 | 0.0084133 |  | 0.23968 | 3.3377e-08 | 0.23424 | 37987.2915 | 0.060134 | 0.83504 | 0.0010117 | 0.46821 | 1.1489e-06 | 0.5703 | 45498.1681 | 0.11425 | 0.87051 | 0.035784 |  | 0.045209
0.13425 | 2.4242e-07 | 0.14941 | 14217.2386 | 0.39225 | 0.85586 | 0.0045358 |  | 0.90225 | 1.7989e-07 | 0.32116 | 40019.0624 | 0.94332 | 0.96621 | 0.0040103 | 0.026818 | 3.6347e-07 | 0.56424 | 45358.2616 | 0.49851 | 0.9301 | 0.0098925 |  | 0.018439
0.86768 | 1.3448e-06 | 0.36989 | 16375.9701 | 0.66314 | 0.89348 | 0.022388 |  | 0.68017 | 1.0009e-07 | 0.70764 | 48986.4633 | 0.12932 | 0.85984 | 0.0033369 | 0.18204 | 7.1986e-07 | 0.47355 | 43335.5337 | 0.1767 | 0.88609 | 0.021004 |  | 0.046729
0.53835 | 6.8645e-07 | 0.66479 | 19055.5536 | 0.32773 | 0.8455 | 0.01482 |  | 0.09195 | 1.5662e-08 | 0.82856 | 53087.6233 | 0.49557 | 0.9148 | 0.00049719 | 0.86206 | 2.0073e-06 | 0.34224 | 40486.6925 | 0.2256 | 0.89537 | 0.054782 |  | 0.0701
0.27299 | 3.8957e-07 | 0.60247 | 18433.9386 | 0.33016 | 0.84591 | 0.0082958 |  | 0.90969 | 1.8504e-07 | 0.37577 | 41219.9839 | 0.73769 | 0.93942 | 0.0045646 | 0.51446 | 1.2203e-06 | 0.24936 | 38357.2477 | 0.6004 | 0.94013 | 0.028403 |  | 0.041263
0.42875 | 5.5562e-07 | 0.59762 | 18387.71 | 0.71426 | 0.90049 | 0.0094434 |  | 0.082463 | 1.4445e-08 | 0.84928 | 53996.1364 | 0.20538 | 0.87647 | 0.00049813 | 0.24158 | 8.1411e-07 | 0.93946 | 59877.5534 | 0.68995 | 0.94862 | 0.026785 |  | 0.036727
0.09234 | 1.9293e-07 | 0.80814 | 20831.3655 | 0.87601 | 0.92602 | 0.0031111 |  | 0.035385 | 7.8551e-09 | 0.0014875 | 24244.3424 | 0.018743 | 0.80146 | 0.00021294 | 0.95087 | 2.5375e-06 | 0.34499 | 40547.1676 | 0.3167 | 0.90915 | 0.066965 |  | 0.070289
0.89985 | 1.4794e-06 | 0.369 | 16368.2444 | 0.13987 | 0.80418 | 0.035114 |  | 0.39334 | 5.246e-08 | 0.17592 | 36453.6078 | 0.52388 | 0.91776 | 0.0012555 | 0.47734 | 1.1628e-06 | 0.065351 | 32458.9494 | 0.79828 | 0.95917 | 0.022259 |  | 0.058629
0.90099 | 1.4849e-06 | 0.21815 | 14977.5241 | 0.52635 | 0.87507 | 0.02598 |  | 0.65727 | 9.5193e-08 | 0.6517 | 47476.256 | 0.88476 | 0.95661 | 0.0025235 | 0.84821 | 1.9548e-06 | 0.82394 | 52896.8734 | 0.92398 | 0.97395 | 0.054816 |  | 0.083319
0.39327 | 5.1641e-07 | 0.78525 | 20496.5463 | 0.38668 | 0.855 | 0.011084 |  | 0.99847 | 4.3838e-07 | 0.31114 | 39794.2612 | 0.75836 | 0.94159 | 0.010456 | 0.10254 | 5.744e-07 | 0.51626 | 44273.9305 | 0.23159 | 0.89639 | 0.016611 |  | 0.038152
0.58843 | 7.5325e-07 | 0.30413 | 15795.5804 | 0.71285 | 0.90029 | 0.011935 |  | 0.2242 | 3.1543e-08 | 0.42712 | 42330.3278 | 0.30122 | 0.89168 | 0.00089459 | 0.2171 | 7.7624e-07 | 0.51406 | 44225.1918 | 0.80588 | 0.95995 | 0.0192 |  | 0.03203
0.06112 | 1.5159e-07 | 0.06172 | 12860.3134 | 0.77402 | 0.90907 | 0.0020936 |  | 0.48578 | 6.5386e-08 | 0.775 | 51076.5008 | 0.84842 | 0.95183 | 0.0018653 | 0.73639 | 1.6341e-06 | 0.014263 | 28339.2569 | 0.8636 | 0.96621 | 0.027209 |  | 0.031168
0.53815 | 6.8619e-07 | 0.32667 | 15997.3131 | 0.062687 | 0.77189 | 0.017949 |  | 0.94974 | 2.2269e-07 | 0.02352 | 29519.6897 | 0.85502 | 0.95266 | 0.0040549 | 0.042106 | 4.2075e-07 | 0.82402 | 52900.0606 | 0.019805 | 0.81576 | 0.015869 |  | 0.037873
0.1714 | 2.8328e-07 | 0.57447 | 18170.4617 | 0.58373 | 0.88282 | 0.0051801 |  | 0.069753 | 1.2773e-08 | 0.751 | 50288.3839 | 0.6455 | 0.93005 | 0.00037698 | 0.36641 | 9.9834e-07 | 0.85139 | 54094.0795 | 0.69429 | 0.94903 | 0.030083 |  | 0.03564
0.77982 | 1.0903e-06 | 0.43032 | 16896.972 | 0.97681 | 0.95424 | 0.013161 |  | 0.87227 | 1.6238e-07 | 0.6984 | 48725.7669 | 0.84814 | 0.9518 | 0.0044509 | 0.16683 | 6.9432e-07 | 0.72706 | 49552.5369 | 0.76529 | 0.95587 | 0.019128 |  | 0.03674
0.28636 | 4.0341e-07 | 0.021148 | 11659.5709 | 0.51456 | 0.87346 | 0.006526 |  | 0.31957 | 4.3035e-08 | 0.066859 | 32535.2928 | 0.7018 | 0.93572 | 0.00089741 | 0.52458 | 1.2363e-06 | 0.36582 | 41003.4604 | 0.73183 | 0.95262 | 0.029277 |  | 0.036701
0.087454 | 1.8679e-07 | 0.80487 | 20781.7853 | 0.25477 | 0.83217 | 0.0043614 |  | 0.69561 | 1.0357e-07 | 0.80733 | 52240.9257 | 0.67316 | 0.93282 | 0.0031331 | 0.92512 | 2.3279e-06 | 0.011407 | 27852.865 | 0.53378 | 0.93365 | 0.043799 |  | 0.051293
0.97928 | 2.2042e-06 | 0.1237 | 13886.3081 | 0.096826 | 0.78881 | 0.052851 |  | 0.33191 | 4.4571e-08 | 0.031621 | 30287.8705 | 0.35707 | 0.89904 | 0.001001 | 0.27387 | 8.6275e-07 | 0.46677 | 43188.1609 | 0.7427 | 0.95366 | 0.021269 |  | 0.075121
0.76098 | 1.048e-06 | 0.68857 | 19309.6326 | 0.95856 | 0.94651 | 0.014487 |  | 0.11597 | 1.8656e-08 | 0.42367 | 42255.7433 | 0.63226 | 0.92872 | 0.00048255 | 0.70073 | 1.5548e-06 | 0.54731 | 44971.0566 | 0.040396 | 0.83686 | 0.051477 |  | 0.066446
0.2681 | 3.845e-07 | 0.87453 | 22018.0454 | 0.20803 | 0.82221 | 0.009469 |  | 0.35801 | 4.7868e-08 | 0.28059 | 39096.1693 | 0.31171 | 0.89313 | 0.0012839 | 0.2507 | 8.2797e-07 | 0.71909 | 49317.3065 | 0.27233 | 0.90287 | 0.025479 |  | 0.036231
0.91462 | 1.5553e-06 | 0.16483 | 14400.8212 | 0.53193 | 0.87583 | 0.026726 |  | 0.60383 | 8.4779e-08 | 0.13264 | 35143.7963 | 0.070717 | 0.84007 | 0.0024393 | 0.63436 | 1.4236e-06 | 0.44105 | 42631.1709 | 0.15656 | 0.88165 | 0.041512 |  | 0.070677
0.44823 | 5.7768e-07 | 0.59615 | 18373.7654 | 0.50349 | 0.87194 | 0.011108 |  | 0.43042 | 5.7466e-08 | 0.87443 | 55243.96 | 0.64009 | 0.92951 | 0.0018303 | 0.73098 | 1.6216e-06 | 0.41418 | 42051.0713 | 0.46075 | 0.92617 | 0.042065 |  | 0.055003
0.67522 | 8.8529e-07 | 0.89142 | 22400.2241 | 0.46012 | 0.86586 | 0.018988 |  | 0.92436 | 1.965e-07 | 0.44238 | 42659.7572 | 0.30559 | 0.89229 | 0.005594 | 0.91306 | 2.2516e-06 | 0.89691 | 56546.8426 | 0.95289 | 0.97866 | 0.066512 |  | 0.091094
0.0085464 | 5.2056e-08 | 0.88076 | 22153.7547 | 0.94656 | 0.94257 | 0.0008054 |  | 0.66009 | 9.578e-08 | 0.99788 | 77800.3742 | 0.23384 | 0.88145 | 0.0042788 | 0.41703 | 1.0724e-06 | 0.47948 | 43464.9306 | 0.64905 | 0.94475 | 0.02721 |  | 0.032294
0.7007 | 9.2942e-07 | 0.94674 | 24168.7004 | 0.37224 | 0.85275 | 0.021566 |  | 0.83841 | 1.4679e-07 | 0.7 | 48770.4008 | 0.93614 | 0.96482 | 0.0039059 | 0.66672 | 1.4853e-06 | 0.23122 | 37912.3543 | 0.80369 | 0.95973 | 0.032262 |  | 0.057734
0.22686 | 3.4178e-07 | 0.86733 | 21867.7493 | 0.45577 | 0.86524 | 0.0072681 |  | 0.43574 | 5.8204e-08 | 0.79851 | 51909.6115 | 0.28402 | 0.88924 | 0.0019081 | 0.91594 | 2.2689e-06 | 0.36268 | 40934.97 | 0.004225 | 0.77377 | 0.080899 |  | 0.090075
0.62798 | 8.1041e-07 | 0.23626 | 15158.5875 | 0.49781 | 0.87115 | 0.014498 |  | 0.3164 | 4.2644e-08 | 0.64171 | 47221.6356 | 0.26192 | 0.88594 | 0.0013181 | 0.077638 | 5.1906e-07 | 0.58827 | 45918.2487 | 0.18451 | 0.8877 | 0.015685 |  | 0.031501
0.8216 | 1.197e-06 | 0.91362 | 22986.7295 | 0.91056 | 0.9332 | 0.019844 |  | 0.22698 | 3.1873e-08 | 0.22539 | 37766.4544 | 0.4297 | 0.90763 | 0.00080415 | 0.14311 | 6.5273e-07 | 0.26292 | 38681.8036 | 0.36256 | 0.91502 | 0.016411 |  | 0.037059
0.07416 | 1.6953e-07 | 0.58867 | 18303.0778 | 0.79547 | 0.91233 | 0.0027175 |  | 0.58662 | 8.1681e-08 | 0.41822 | 42138.2004 | 0.74463 | 0.94014 | 0.0020462 | 0.38448 | 1.0247e-06 | 0.47759 | 43423.5955 | 0.82606 | 0.96206 | 0.024809 |  | 0.029573
0.55809 | 7.1213e-07 | 0.18781 | 14658.8309 | 0.54778 | 0.87798 | 0.012194 |  | 0.19542 | 2.8146e-08 | 0.94536 | 60493.5768 | 0.54164 | 0.91959 | 0.00098114 | 0.81045 | 1.8297e-06 | 0.44238 | 42659.7694 | 0.21898 | 0.89421 | 0.051855 |  | 0.065031
0.37777 | 4.9961e-07 | 0.072687 | 13079.3144 | 0.90085 | 0.93105 | 0.0060595 |  | 0.22852 | 3.2054e-08 | 0.86952 | 54985.7582 | 0.68875 | 0.9344 | 0.0010077 | 0.56361 | 1.2998e-06 | 0.35727 | 40816.7057 | 0.70775 | 0.95031 | 0.030866 |  | 0.037933
0.4952 | 6.3283e-07 | 0.45593 | 17117.5878 | 0.43049 | 0.86158 | 0.01234 |  | 0.32276 | 4.3431e-08 | 0.44237 | 42659.6623 | 0.39399 | 0.90352 | 0.0012041 | 0.93592 | 2.4063e-06 | 0.018577 | 28945.9133 | 0.54897 | 0.93515 | 0.046238 |  | 0.059782
0.17119 | 2.8306e-07 | 0.13392 | 14022.114 | 0.66042 | 0.89311 | 0.0044229 |  | 0.84675 | 1.5032e-07 | 0.15226 | 35762.0271 | 0.29001 | 0.8901 | 0.0038395 | 0.79333 | 1.7797e-06 | 0.22053 | 37643.5873 | 0.70943 | 0.95047 | 0.03956 |  | 0.047822
0.21559 | 3.3003e-07 | 0.31443 | 15888.262 | 0.562 | 0.8799 | 0.0057792 |  | 0.3593 | 4.8033e-08 | 0.094721 | 33777.6381 | 0.34651 | 0.89771 | 0.0011586 | 0.13153 | 6.3147e-07 | 0.86374 | 54690.9543 | 0.95923 | 0.97988 | 0.018033 |  | 0.024971
0.90907 | 1.5255e-06 | 0.76778 | 20258.1261 | 0.46745 | 0.8669 | 0.031181 |  | 0.34156 | 4.5781e-08 | 0.98851 | 69201.0816 | 0.8162 | 0.94798 | 0.0017103 | 0.99056 | 3.3021e-06 | 0.75232 | 50330.1017 | 0.36937 | 0.91585 | 0.10045 |  | 0.13334
0.18154 | 2.9414e-07 | 0.48356 | 17357.0488 | 0.88147 | 0.92708 | 0.0042455 |  | 0.47135 | 6.3265e-08 | 0.95303 | 61389.835 | 0.74976 | 0.94068 | 0.0021555 | 0.18344 | 7.2216e-07 | 0.29916 | 39522.9011 | 0.86881 | 0.96681 | 0.015897 |  | 0.022298
0.80081 | 1.1415e-06 | 0.82231 | 21053.8277 | 0.46732 | 0.86688 | 0.023727 |  | 0.77706 | 1.2509e-07 | 0.35567 | 40781.6724 | 0.66208 | 0.93171 | 0.0031249 | 0.26112 | 8.437e-07 | 0.72926 | 49618.3582 | 0.025923 | 0.82357 | 0.030278 |  | 0.05713
0.8252 | 1.2073e-06 | 0.34061 | 16120.3536 | 0.90518 | 0.932 | 0.016261 |  | 0.12505 | 1.9765e-08 | 0.001423 | 24178.5235 | 0.21591 | 0.87837 | 0.00042047 | 0.32444 | 9.372e-07 | 0.72967 | 49630.5024 | 0.36259 | 0.91502 | 0.028257 |  | 0.044938
0.57551 | 7.3548e-07 | 0.26574 | 15442.0301 | 0.63907 | 0.89023 | 0.012127 |  | 0.24077 | 3.3506e-08 | 0.54579 | 44936.4517 | 0.35491 | 0.89877 | 0.00097375 | 0.26997 | 8.5694e-07 | 0.51411 | 44226.2454 | 0.89246 | 0.96968 | 0.020651 |  | 0.033752
0.95692 | 1.8735e-06 | 0.66739 | 19082.8511 | 0.4896 | 0.87001 | 0.036886 |  | 0.27309 | 3.7367e-08 | 0.38604 | 41442.7807 | 0.013146 | 0.79195 | 0.0012942 | 0.45175 | 1.1241e-06 | 0.49389 | 43780.2498 | 0.47667 | 0.92784 | 0.029935 |  | 0.068116
0.25868 | 3.7476e-07 | 0.53578 | 17817.9451 | 0.90022 | 0.93092 | 0.005376 |  | 0.23265 | 3.2544e-08 | 0.96178 | 62589.0985 | 0.10816 | 0.85379 | 0.0012864 | 0.40405 | 1.0533e-06 | 0.9147 | 57760.5877 | 0.1579 | 0.88196 | 0.037722 |  | 0.044384
0.83786 | 1.2447e-06 | 0.80981 | 20856.8368 | 0.021908 | 0.73501 | 0.038435 |  | 0.92094 | 1.9364e-07 | 0.57476 | 45601.8476 | 0.022413 | 0.80636 | 0.0068451 | 0.49838 | 1.1952e-06 | 0.8784 | 55459.482 | 0.7765 | 0.95698 | 0.03622 |  | 0.0815
0.53383 | 6.8068e-07 | 0.14169 | 14121.4452 | 0.48558 | 0.86945 | 0.011963 |  | 0.75644 | 1.1904e-07 | 0.17137 | 36324.6106 | 0.78266 | 0.94421 | 0.0026232 | 0.99275 | 3.4183e-06 | 0.91571 | 57835.5182 | 0.41873 | 0.92159 | 0.11458 |  | 0.12916
0.53472 | 6.8181e-07 | 0.82948 | 21171.8207 | 0.19826 | 0.81992 | 0.016673 |  | 0.90635 | 1.8268e-07 | 0.58134 | 45755.2916 | 0.21644 | 0.87846 | 0.0056162 | 8.148e-05 | 7.1656e-08 | 0.179 | 36540.0075 | 0.61229 | 0.94126 | 0.001601 |  | 0.02389
0.60954 | 7.8321e-07 | 0.13109 | 13985.0578 | 0.34548 | 0.84846 | 0.015044 |  | 0.96433 | 2.4443e-07 | 0.76754 | 50825.5569 | 0.25347 | 0.88463 | 0.0079653 | 0.10234 | 5.7397e-07 | 0.62603 | 46829.604 | 0.53491 | 0.93376 | 0.01588 |  | 0.038889
0.78769 | 1.109e-06 | 0.91554 | 23043.5715 | 0.052616 | 0.76539 | 0.032571 |  | 0.99031 | 3.257e-07 | 0.68711 | 48413.4353 | 0.62578 | 0.92808 | 0.0093693 | 0.80247 | 1.806e-06 | 0.75036 | 50268.0322 | 0.34147 | 0.91239 | 0.055275 |  | 0.097216
0.13294 | 2.4094e-07 | 0.65887 | 18993.9315 | 0.54542 | 0.87766 | 0.0045903 |  | 0.080589 | 1.4202e-08 | 0.77475 | 51068.1942 | 0.2636 | 0.8862 | 0.00046294 | 0.87461 | 2.059e-06 | 0.99212 | 71175.5277 | 0.80693 | 0.96006 | 0.077552 |  | 0.082605
0.55343 | 7.0599e-07 | 0.38015 | 16464.8075 | 0.44687 | 0.86396 | 0.013435 |  | 0.14212 | 2.1825e-08 | 0.014914 | 28439.2821 | 0.41814 | 0.90632 | 0.00046038 | 0.054086 | 4.5766e-07 | 0.33939 | 40423.9056 | 0.68933 | 0.94856 | 0.010837 |  | 0.024732
0.39892 | 5.2257e-07 | 0.54599 | 17909.862 | 0.97648 | 0.95407 | 0.0065673 |  | 0.56622 | 7.8144e-08 | 0.62232 | 46738.1753 | 0.59834 | 0.92533 | 0.002201 | 0.74955 | 1.6654e-06 | 0.033979 | 30483.5973 | 0.48436 | 0.92864 | 0.033982 |  | 0.042751
0.49056 | 6.2724e-07 | 0.65172 | 18920.337 | 0.59782 | 0.88471 | 0.011585 |  | 0.24086 | 3.3518e-08 | 0.18035 | 36577.5597 | 0.7146 | 0.93703 | 0.00075929 | 0.51681 | 1.224e-06 | 0.4213 | 42204.739 | 0.6063 | 0.94069 | 0.030657 |  | 0.043001
0.46183 | 5.9335e-07 | 0.65543 | 18958.3939 | 0.15309 | 0.80813 | 0.014518 |  | 0.2945 | 3.9958e-08 | 0.62737 | 46862.8504 | 0.21478 | 0.87817 | 0.0012487 | 0.34785 | 9.7132e-07 | 0.10692 | 34247.9811 | 0.87754 | 0.96784 | 0.018834 |  | 0.034601
0.45092 | 5.8076e-07 | 0.51785 | 17658.1722 | 0.017712 | 0.7281 | 0.017566 |  | 0.36247 | 4.844e-08 | 0.97209 | 64374.9261 | 0.22777 | 0.88043 | 0.0018801 | 0.65156 | 1.4559e-06 | 0.83592 | 53399.9546 | 0.64042 | 0.94393 | 0.043844 |  | 0.063291
0.27128 | 3.878e-07 | 0.46328 | 17181.0832 | 0.050037 | 0.76355 | 0.010576 |  | 0.92768 | 1.994e-07 | 0.3766 | 41238.0841 | 0.86916 | 0.95449 | 0.0047192 | 0.49813 | 1.1948e-06 | 0.6093 | 46420.6539 | 0.25972 | 0.90095 | 0.035351 |  | 0.050647
0.59232 | 7.5868e-07 | 0.61943 | 18597.7909 | 0.64393 | 0.89089 | 0.013537 |  | 0.19216 | 2.7762e-08 | 0.35236 | 40709.1067 | 0.51447 | 0.91678 | 0.00072043 | 0.47841 | 1.1644e-06 | 0.77558 | 51096.3912 | 0.36811 | 0.9157 | 0.03584 |  | 0.050097
0.14446 | 2.5385e-07 | 0.14067 | 14108.504 | 0.6571 | 0.89266 | 0.0039855 |  | 0.01814 | 4.9309e-09 | 0.40701 | 41896.2969 | 0.3932 | 0.90343 | 0.00013503 | 0.067565 | 4.942e-07 | 0.43295 | 42456.0352 | 0.44205 | 0.92416 | 0.012978 |  | 0.017099
0.897 | 1.466e-06 | 0.094795 | 13462.1989 | 0.45947 | 0.86577 | 0.025781 |  | 0.21832 | 3.0848e-08 | 0.47477 | 43362.1433 | 0.98123 | 0.97627 | 0.00071709 | 0.032804 | 3.8773e-07 | 0.28922 | 39295.4745 | 0.76424 | 0.95577 | 0.0087834 |  | 0.035282
0.78201 | 1.0954e-06 | 0.085585 | 13310.5107 | 0.58015 | 0.88234 | 0.017724 |  | 0.61693 | 8.7215e-08 | 0.47229 | 43308.1235 | 0.99055 | 0.98067 | 0.0019997 | 0.74473 | 1.6538e-06 | 0.72728 | 49559.2468 | 0.28712 | 0.90504 | 0.050846 |  | 0.070569
0.47351 | 6.07e-07 | 0.89309 | 22440.61 | 0.069429 | 0.77576 | 0.017207 |  | 0.18167 | 2.6523e-08 | 0.7158 | 49221.2914 | 0.14849 | 0.86465 | 0.00087889 | 0.26225 | 8.4539e-07 | 0.79091 | 51633.0895 | 0.97283 | 0.98287 | 0.02272 |  | 0.040806
0.79327 | 1.1226e-06 | 0.24876 | 15280.328 | 0.54733 | 0.87792 | 0.019534 |  | 0.28232 | 3.848e-08 | 0.0052662 | 26329.1471 | 0.49231 | 0.91446 | 0.0007516 | 0.76618 | 1.7068e-06 | 0.39066 | 41542.7437 | 0.98584 | 0.98665 | 0.036975 |  | 0.057261
0.41775 | 5.4333e-07 | 0.98106 | 26508.7308 | 0.034507 | 0.75035 | 0.017286 |  | 0.38058 | 5.0783e-08 | 0.43647 | 42532.1985 | 0.014552 | 0.79465 | 0.0017717 | 0.28467 | 8.7879e-07 | 0.51883 | 44331.1654 | 0.047656 | 0.84195 | 0.028567 |  | 0.047625
0.9436 | 1.7494e-06 | 0.89851 | 22575.4698 | 0.23043 | 0.82716 | 0.042822 |  | 0.74363 | 1.1551e-07 | 0.41544 | 42078.2586 | 0.49269 | 0.9145 | 0.0030878 | 0.57816 | 1.3242e-06 | 0.3597 | 40869.9008 | 0.33338 | 0.91135 | 0.034944 |  | 0.080854
0.39905 | 5.2271e-07 | 0.19288 | 14713.7188 | 0.45138 | 0.86461 | 0.0095243 |  | 0.70285 | 1.0526e-07 | 0.79942 | 51943.2543 | 0.2566 | 0.88512 | 0.003479 | 0.54689 | 1.2722e-06 | 0.80613 | 52195.2171 | 0.20473 | 0.89163 | 0.041682 |  | 0.054686
0.60173 | 7.7199e-07 | 0.18602 | 14639.2995 | 0.067893 | 0.7749 | 0.019601 |  | 0.36659 | 4.8969e-08 | 0.82965 | 53132.959 | 0.23407 | 0.88149 | 0.0016552 | 0.3333 | 9.5012e-07 | 0.97154 | 64266.6992 | 0.43689 | 0.9236 | 0.034557 |  | 0.055813
0.45676 | 5.8748e-07 | 0.60359 | 18444.6715 | 0.049644 | 0.76326 | 0.016319 |  | 0.61636 | 8.7108e-08 | 0.58019 | 45728.3448 | 0.22109 | 0.87928 | 0.0026724 | 0.89225 | 2.1398e-06 | 0.44287 | 42670.3189 | 0.92993 | 0.97484 | 0.049221 |  | 0.068212
0.98777 | 2.4375e-06 | 0.58711 | 18288.41 | 0.57536 | 0.8817 | 0.044914 |  | 0.63259 | 9.0221e-08 | 0.034935 | 30560.0649 | 0.50286 | 0.91557 | 0.0019295 | 0.80744 | 1.8207e-06 | 0.36631 | 41014.0978 | 0.27071 | 0.90262 | 0.049231 |  | 0.096074
0.99729 | 3.0896e-06 | 0.65454 | 18949.2565 | 0.27009 | 0.83515 | 0.069062 |  | 0.02346 | 5.892e-09 | 0.85902 | 54458.0277 | 0.67107 | 0.93261 | 0.0001844 | 0.48946 | 1.1814e-06 | 0.273 | 38919.3719 | 0.33307 | 0.91131 | 0.030128 |  | 0.099375
0.044535 | 1.267e-07 | 0.67031 | 19113.579 | 0.6404 | 0.89041 | 0.0022944 |  | 0.50004 | 6.7528e-08 | 0.55723 | 45197.1357 | 0.031153 | 0.8156 | 0.0023355 | 0.88319 | 2.097e-06 | 0.42615 | 42309.3399 | 0.80791 | 0.96016 | 0.049911 |  | 0.054541
0.36355 | 4.8437e-07 | 0.32375 | 15971.332 | 0.67658 | 0.8953 | 0.0079055 |  | 0.77355 | 1.2403e-07 | 0.81357 | 52482.1129 | 0.43124 | 0.90781 | 0.0039562 | 0.0093149 | 2.6291e-07 | 0.82272 | 52846.948 | 0.88468 | 0.96871 | 0.0074502 |  | 0.019312
0.41768 | 5.4325e-07 | 0.26173 | 15404.2435 | 0.94754 | 0.94287 | 0.0066639 |  | 0.033774 | 7.6017e-09 | 0.64994 | 47430.9826 | 0.4693 | 0.912 | 0.00022301 | 0.1435 | 6.5345e-07 | 0.28403 | 39176.0044 | 0.48471 | 0.92868 | 0.015969 |  | 0.022856
0.97377 | 2.0986e-06 | 0.089986 | 13384.217 | 0.72409 | 0.90186 | 0.030707 |  | 0.79937 | 1.3225e-07 | 0.30165 | 39579.5127 | 0.74176 | 0.93984 | 0.0031568 | 0.76846 | 1.7127e-06 | 0.85269 | 54155.0102 | 0.98349 | 0.98586 | 0.047841 |  | 0.081704
0.10218 | 2.0501e-07 | 0.30803 | 15830.799 | 0.72262 | 0.90165 | 0.0032293 |  | 0.10326 | 1.7084e-08 | 0.38643 | 41451.1232 | 0.47362 | 0.91246 | 0.0004541 | 0.49516 | 1.1902e-06 | 0.81338 | 52474.4416 | 0.94813 | 0.9778 | 0.032848 |  | 0.036531
0.85419 | 1.2972e-06 | 0.38136 | 16475.2801 | 0.52751 | 0.87523 | 0.023531 |  | 0.92174 | 1.9431e-07 | 0.90614 | 57151.8387 | 0.25234 | 0.88445 | 0.0068777 | 0.77753 | 1.7364e-06 | 0.57944 | 45710.8558 | 0.34614 | 0.91298 | 0.04947 |  | 0.079879
0.90486 | 1.5039e-06 | 0.94477 | 24082.3415 | 0.54572 | 0.8777 | 0.032006 |  | 0.95353 | 2.2769e-07 | 0.058771 | 32111.3757 | 0.90073 | 0.95892 | 0.0043249 | 0.92771 | 2.3457e-06 | 0.86019 | 54515.3706 | 0.31915 | 0.90948 | 0.076753 |  | 0.11308
0.54214 | 6.9132e-07 | 0.44772 | 17046.7264 | 0.98093 | 0.9565 | 0.0082703 |  | 0.21383 | 3.0318e-08 | 0.93095 | 59076.2819 | 0.51029 | 0.91635 | 0.0010428 | 0.92737 | 2.3434e-06 | 0.48522 | 43590.2238 | 0.67857 | 0.94754 | 0.059163 |  | 0.068476
0.80286 | 1.1467e-06 | 0.9815 | 26559.6825 | 0.9985 | 0.97641 | 0.017239 |  | 0.69821 | 1.0417e-07 | 0.53828 | 44766.73 | 0.23339 | 0.88137 | 0.0031377 | 0.10693 | 5.8346e-07 | 0.20706 | 37296.9333 | 0.43996 | 0.92393 | 0.013941 |  | 0.034317
0.72992 | 9.8406e-07 | 0.5001 | 17501.6767 | 0.14188 | 0.8048 | 0.023758 |  | 0.74884 | 1.1693e-07 | 0.61432 | 46542.5312 | 0.38572 | 0.90254 | 0.0034542 | 0.78117 | 1.7462e-06 | 0.84897 | 53982.1622 | 0.33353 | 0.91137 | 0.056511 |  | 0.083723
0.50917 | 6.4984e-07 | 0.61724 | 18576.4318 | 0.93183 | 0.9384 | 0.0091709 |  | 0.19193 | 2.7735e-08 | 0.45641 | 42963.3906 | 0.89691 | 0.95835 | 0.00067216 | 0.89128 | 2.135e-06 | 0.73207 | 49702.8146 | 0.037777 | 0.83481 | 0.075189 |  | 0.085032
0.55306 | 7.0551e-07 | 0.49943 | 17495.7445 | 0.048001 | 0.76204 | 0.01941 |  | 0.041198 | 8.7471e-09 | 0.10562 | 34199.4939 | 0.21338 | 0.87792 | 0.00022486 | 0.94938 | 2.5229e-06 | 0.074503 | 32905.3087 | 0.15958 | 0.88234 | 0.062627 |  | 0.082261
0.012454 | 6.3463e-08 | 0.54984 | 17944.7459 | 0.48265 | 0.86904 | 0.0012229 |  | 0.44131 | 5.8979e-08 | 0.79398 | 51744.0173 | 0.41523 | 0.90599 | 0.0018682 | 0.79156 | 1.7747e-06 | 0.51761 | 44303.9945 | 0.28511 | 0.90475 | 0.050378 |  | 0.053469
0.19123 | 3.0444e-07 | 0.80852 | 20837.048 | 0.4367 | 0.86249 | 0.0064029 |  | 0.21316 | 3.0239e-08 | 0.32686 | 40146.0926 | 0.088753 | 0.8473 | 0.00091879 | 0.715 | 1.5856e-06 | 0.4105 | 41971.612 | 0.36521 | 0.91535 | 0.042217 |  | 0.049539
0.68817 | 9.0735e-07 | 0.73178 | 19804.0098 | 0.66438 | 0.89364 | 0.016483 |  | 0.16654 | 2.4735e-08 | 0.073045 | 32836.7563 | 0.77634 | 0.94352 | 0.00050554 | 0.85287 | 1.972e-06 | 0.95992 | 62315.3566 | 0.46194 | 0.92629 | 0.069647 |  | 0.086635
0.65497 | 8.5219e-07 | 0.55627 | 18003.1513 | 0.48258 | 0.86903 | 0.016443 |  | 0.63542 | 9.0777e-08 | 0.81476 | 52528.6068 | 0.7673 | 0.94255 | 0.0027041 | 0.85449 | 1.9781e-06 | 0.90083 | 56798.3471 | 0.55184 | 0.93543 | 0.063738 |  | 0.082885
0.87106 | 1.3574e-06 | 0.515 | 17632.8878 | 0.6273 | 0.88865 | 0.023876 |  | 0.21029 | 2.99e-08 | 0.54414 | 44899.1656 | 0.18145 | 0.87186 | 0.00092086 | 0.57186 | 1.3136e-06 | 0.45969 | 43034.4481 | 0.53951 | 0.93421 | 0.033975 |  | 0.058771
0.15257 | 2.6282e-07 | 0.74994 | 20027.4379 | 0.39362 | 0.85607 | 0.0055667 |  | 0.38967 | 5.1975e-08 | 0.57656 | 45643.5655 | 0.54097 | 0.91952 | 0.0014571 | 0.74933 | 1.6648e-06 | 0.98271 | 67014.2406 | 0.99992 | 0.99781 | 0.055981 |  | 0.063005
0.64213 | 8.3201e-07 | 0.084982 | 13300.2172 | 0.21929 | 0.82474 | 0.017337 |  | 0.70331 | 1.0537e-07 | 0.11025 | 34370.8652 | 0.55388 | 0.92084 | 0.0023981 | 0.29864 | 8.9941e-07 | 0.21628 | 37535.374 | 0.68998 | 0.94862 | 0.020061 |  | 0.039796
0.38089 | 5.0297e-07 | 0.98215 | 26636.6685 | 0.30259 | 0.84114 | 0.012634 |  | 0.76801 | 1.2238e-07 | 0.84768 | 53922.5677 | 0.6103 | 0.92653 | 0.0038446 | 0.24736 | 8.229e-07 | 0.98794 | 68942.6304 | 0.7039 | 0.94994 | 0.030555 |  | 0.047034
0.24825 | 3.6397e-07 | 0.20498 | 14841.8831 | 0.89089 | 0.92897 | 0.004774 |  | 0.015895 | 4.5016e-09 | 0.038004 | 30795.8183 | 0.7456 | 0.94024 | 8.8737e-05 | 0.23789 | 8.0846e-07 | 0.19746 | 37043.7317 | 0.24953 | 0.89934 | 0.020595 |  | 0.025458
0.35653 | 4.7689e-07 | 0.239 | 15185.5134 | 0.18934 | 0.81777 | 0.010574 |  | 0.65929 | 9.5612e-08 | 0.75431 | 50393.7045 | 0.011093 | 0.7875 | 0.003677 | 0.52001 | 1.2291e-06 | 0.50161 | 43949.9373 | 0.65385 | 0.9452 | 0.031428 |  | 0.045679
0.56003 | 7.147e-07 | 0.24688 | 15262.186 | 0.35591 | 0.85015 | 0.014018 |  | 0.85534 | 1.5415e-07 | 0.1185 | 34665.1882 | 0.48026 | 0.91317 | 0.0036123 | 0.80515 | 1.8139e-06 | 0.67404 | 48060.6385 | 0.21541 | 0.89358 | 0.055859 |  | 0.07349
0.61758 | 7.9494e-07 | 0.96543 | 25172.2941 | 0.7634 | 0.9075 | 0.015521 |  | 0.741 | 1.1481e-07 | 0.4888 | 43668.5973 | 0.83726 | 0.95046 | 0.0028808 | 0.38931 | 1.0318e-06 | 0.15856 | 35951.3717 | 0.20143 | 0.89101 | 0.026376 |  | 0.044778
0.57942 | 7.4082e-07 | 0.72479 | 19720.7556 | 0.59843 | 0.88479 | 0.01394 |  | 0.70738 | 1.0633e-07 | 0.28988 | 39310.7129 | 0.99798 | 0.98754 | 0.00218 | 0.74154 | 1.6462e-06 | 0.55808 | 45216.6075 | 0.34826 | 0.91325 | 0.046499 |  | 0.062619
0.071593 | 1.6609e-07 | 0.96991 | 25486.3873 | 0.55096 | 0.87841 | 0.0036282 |  | 0.99159 | 3.3444e-07 | 0.27827 | 39042.3462 | 0.24233 | 0.88285 | 0.0091959 | 0.61854 | 1.3947e-06 | 0.082057 | 33247.2307 | 0.80154 | 0.95951 | 0.027193 |  | 0.040017
0.077979 | 1.7458e-07 | 0.91041 | 22894.6968 | 0.67732 | 0.8954 | 0.0033892 |  | 0.48013 | 6.4551e-08 | 0.46717 | 43196.9184 | 0.33961 | 0.89683 | 0.0018338 | 0.57681 | 1.3219e-06 | 0.32007 | 39994.4828 | 0.64123 | 0.94401 | 0.031438 |  | 0.036661
0.98697 | 2.4099e-06 | 0.32694 | 15999.7282 | 0.51515 | 0.87354 | 0.043536 |  | 0.93925 | 2.1059e-07 | 0.044876 | 31277.6289 | 0.017041 | 0.79888 | 0.0063411 | 0.63057 | 1.4166e-06 | 0.67023 | 47959.4895 | 0.27507 | 0.90328 | 0.042686 |  | 0.092564
0.93659 | 1.695e-06 | 0.4442 | 17016.3889 | 0.2347 | 0.82806 | 0.037472 |  | 0.32784 | 4.4063e-08 | 0.059084 | 32128.4688 | 0.14035 | 0.86267 | 0.0011407 | 0.3622 | 9.922e-07 | 0.82393 | 52896.1659 | 0.63702 | 0.94361 | 0.029663 |  | 0.068276
0.50003 | 6.3867e-07 | 0.7169 | 19628.3378 | 0.74244 | 0.90446 | 0.011014 |  | 0.47702 | 6.4093e-08 | 0.37632 | 41231.848 | 0.36973 | 0.90061 | 0.0017481 | 0.69172 | 1.5359e-06 | 0.52003 | 44357.9332 | 0.35852 | 0.91452 | 0.042652 |  | 0.055415
0.78058 | 1.0921e-06 | 0.49752 | 17478.9918 | 0.9556 | 0.94548 | 0.01424 |  | 0.18568 | 2.6998e-08 | 0.16906 | 36258.3459 | 0.86167 | 0.95351 | 0.00057664 | 0.73988 | 1.6423e-06 | 0.89658 | 56526.1024 | 0.86212 | 0.96604 | 0.049726 |  | 0.064542
0.30198 | 4.1962e-07 | 0.81626 | 20957.3187 | 0.075574 | 0.77902 | 0.011548 |  | 0.25099 | 3.4723e-08 | 0.85727 | 54373.1761 | 0.41928 | 0.90645 | 0.0011402 | 0.50532 | 1.206e-06 | 0.2735 | 38931.1689 | 0.18417 | 0.88763 | 0.032708 |  | 0.045396
0.61609 | 7.9276e-07 | 0.84476 | 21436.2618 | 0.58046 | 0.88238 | 0.015666 |  | 0.10264 | 1.7008e-08 | 0.33521 | 40331.3949 | 0.16998 | 0.86948 | 0.00049267 | 0.77094 | 1.7191e-06 | 0.18659 | 36749.9004 | 0.15796 | 0.88197 | 0.045634 |  | 0.061792
0.63118 | 8.1524e-07 | 0.68237 | 19242.2756 | 0.19414 | 0.81894 | 0.019354 |  | 0.22326 | 3.1432e-08 | 0.55297 | 45099.7816 | 0.58201 | 0.92369 | 0.00086484 | 0.35193 | 9.7725e-07 | 0.071061 | 32741.9899 | 0.1434 | 0.87849 | 0.024457 |  | 0.044676
0.64921 | 8.4306e-07 | 0.060187 | 12827.6473 | 0.41888 | 0.85987 | 0.014998 |  | 0.54275 | 7.424e-08 | 0.75959 | 50564.0912 | 0.29018 | 0.89013 | 0.0023853 | 0.037474 | 4.049e-07 | 0.12025 | 34726.4378 | 0.533 | 0.93357 | 0.0089196 |  | 0.026303
0.93578 | 1.6892e-06 | 0.2081 | 14874.3641 | 0.48063 | 0.86876 | 0.030334 |  | 0.04733 | 9.6549e-09 | 0.15707 | 35906.9632 | 0.70808 | 0.93636 | 0.00021613 | 0.24484 | 8.1907e-07 | 0.4597 | 43034.7903 | 0.19024 | 0.88884 | 0.023641 |  | 0.054191
0.46383 | 5.9568e-07 | 0.70415 | 19482.5034 | 0.12186 | 0.79829 | 0.015158 |  | 0.86501 | 1.5873e-07 | 0.022721 | 29433.5559 | 0.77592 | 0.94348 | 0.0029898 | 0.75302 | 1.6738e-06 | 0.42573 | 42300.2369 | 0.97317 | 0.98295 | 0.037298 |  | 0.055446
0.463 | 5.9471e-07 | 0.090434 | 13391.5953 | 0.28643 | 0.83822 | 0.011766 |  | 0.48946 | 6.5935e-08 | 0.26472 | 38724.4286 | 0.50554 | 0.91585 | 0.0016553 | 0.9383 | 2.4252e-06 | 0.35199 | 40700.9804 | 0.31167 | 0.90847 | 0.064282 |  | 0.077703
0.79098 | 1.117e-06 | 0.14229 | 14129.0221 | 0.95092 | 0.94393 | 0.012934 |  | 0.63885 | 9.1453e-08 | 0.33128 | 40244.3703 | 0.91769 | 0.96158 | 0.0020773 | 0.75661 | 1.6827e-06 | 0.00029625 | 22092.5215 | 0.97613 | 0.98371 | 0.020686 |  | 0.035698
0.66661 | 8.7102e-07 | 0.85771 | 21677.2453 | 0.36783 | 0.85206 | 0.019332 |  | 0.13718 | 2.1231e-08 | 0.89409 | 56371.388 | 0.77829 | 0.94373 | 0.0006694 | 0.83039 | 1.8929e-06 | 0.035334 | 30591.5155 | 0.12187 | 0.87274 | 0.046369 |  | 0.066371
0.17625 | 2.8849e-07 | 0.32752 | 16004.8408 | 0.90591 | 0.93216 | 0.0038665 |  | 0.50693 | 6.8579e-08 | 0.37105 | 41117.3476 | 0.70927 | 0.93648 | 0.0017019 | 0.63277 | 1.4206e-06 | 0.073024 | 32835.7686 | 0.88093 | 0.96825 | 0.026534 |  | 0.032103
0.034747 | 1.1036e-07 | 0.48044 | 17329.9494 | 0.49938 | 0.87137 | 0.0020768 |  | 0.94627 | 2.1844e-07 | 0.012425 | 28036.2678 | 0.96664 | 0.9716 | 0.0035186 | 0.69184 | 1.5361e-06 | 0.12939 | 35036.3856 | 0.5026 | 0.93052 | 0.03439 |  | 0.039985
0.81491 | 1.1786e-06 | 0.044834 | 12463.6256 | 0.79596 | 0.9124 | 0.015745 |  | 0.45595 | 6.1047e-08 | 0.82633 | 52995.0996 | 0.81029 | 0.9473 | 0.0018142 | 0.35352 | 9.7956e-07 | 0.34844 | 40623.1965 | 0.45868 | 0.92595 | 0.024778 |  | 0.042337
0.92028 | 1.5877e-06 | 0.029926 | 12011.5407 | 0.81404 | 0.91524 | 0.020516 |  | 0.78812 | 1.2855e-07 | 0.38786 | 41482.2459 | 0.32736 | 0.89523 | 0.0035669 | 0.6245 | 1.4055e-06 | 0.29769 | 39489.3906 | 0.2937 | 0.90598 | 0.036718 |  | 0.060801
0.96809 | 2.0101e-06 | 0.4137 | 16753.9921 | 0.66717 | 0.89402 | 0.033716 |  | 0.65281 | 9.4271e-08 | 0.8908 | 56170.8641 | 0.57193 | 0.92267 | 0.0030815 | 0.6077 | 1.3753e-06 | 0.93329 | 59287.3668 | 0.94919 | 0.97799 | 0.042525 |  | 0.079322
0.23182 | 3.4694e-07 | 0.791 | 20578.0324 | 0.74016 | 0.90414 | 0.0061409 |  | 0.40079 | 5.3449e-08 | 0.923 | 58401.8429 | 0.40465 | 0.90477 | 0.001858 | 0.89104 | 2.1339e-06 | 0.85214 | 54129.2627 | 0.10055 | 0.86613 | 0.075045 |  | 0.083044
0.2135 | 3.2785e-07 | 0.45093 | 17074.4558 | 0.26363 | 0.83391 | 0.0071042 |  | 0.35581 | 4.7588e-08 | 0.97247 | 64451.8633 | 0.88775 | 0.95703 | 0.0016468 | 0.4338 | 1.0973e-06 | 0.9358 | 59520.8719 | 0.18335 | 0.88746 | 0.039797 |  | 0.048548
0.03794 | 1.1586e-07 | 0.99982 | 35689.7179 | 0.33868 | 0.84734 | 0.0033014 |  | 0.39417 | 5.2569e-08 | 0.02027 | 29154.3168 | 0.26446 | 0.88633 | 0.0012027 | 0.77991 | 1.7428e-06 | 0.21859 | 37594.1579 | 0.017582 | 0.81235 | 0.055259 |  | 0.059763
0.96124 | 1.9218e-06 | 0.85323 | 21591.999 | 0.084249 | 0.78326 | 0.052738 |  | 0.93667 | 2.0792e-07 | 0.36218 | 40924.116 | 0.86805 | 0.95434 | 0.0048918 | 0.42283 | 1.081e-06 | 0.41828 | 42139.4657 | 0.081221 | 0.859 | 0.032917 |  | 0.090547
0.96848 | 2.0157e-06 | 0.27132 | 15494.4118 | 0.2544 | 0.83209 | 0.042643 |  | 0.92335 | 1.9564e-07 | 0.27471 | 38959.3927 | 0.17888 | 0.87133 | 0.0055258 | 0.64395 | 1.4415e-06 | 0.23109 | 37909.0668 | 0.003787 | 0.77095 | 0.049987 |  | 0.098156
0.16454 | 2.7587e-07 | 0.23048 | 15101.4767 | 0.20631 | 0.82181 | 0.0060181 |  | 0.97102 | 2.5751e-07 | 0.087266 | 33471.2777 | 0.57593 | 0.92307 | 0.0057135 | 0.46511 | 1.1442e-06 | 0.99826 | 78785.8597 | 0.20919 | 0.89245 | 0.051005 |  | 0.062737
0.027509 | 9.7088e-08 | 0.56492 | 18082.3231 | 0.31752 | 0.84375 | 0.0020695 |  | 0.20558 | 2.9344e-08 | 0.7986 | 51913.1376 | 0.28027 | 0.88869 | 0.00096301 | 0.20078 | 7.5036e-07 | 0.16184 | 36048.2648 | 0.59681 | 0.93978 | 0.016668 |  | 0.019701
0.17028 | 2.8208e-07 | 0.56158 | 18051.7359 | 0.50137 | 0.87164 | 0.0053908 |  | 0.84723 | 1.5053e-07 | 0.20803 | 37322.1758 | 0.7858 | 0.94455 | 0.0033844 | 0.4449 | 1.1138e-06 | 0.45826 | 43003.467 | 0.28684 | 0.905 | 0.030943 |  | 0.039718
0.8696 | 1.3519e-06 | 0.93958 | 23867.0945 | 0.78013 | 0.90999 | 0.025341 |  | 0.063724 | 1.196e-08 | 0.028933 | 30051.1788 | 0.067406 | 0.83857 | 0.00031982 | 0.42424 | 1.0831e-06 | 0.15923 | 35971.1618 | 0.04956 | 0.84317 | 0.031305 |  | 0.056966
0.77346 | 1.0757e-06 | 0.93972 | 23872.6975 | 0.87251 | 0.92535 | 0.018915 |  | 0.66371 | 9.6539e-08 | 0.33852 | 40404.6245 | 0.99625 | 0.98519 | 0.0020467 | 0.52298 | 1.2338e-06 | 0.23307 | 37958.3083 | 0.51744 | 0.93202 | 0.029172 |  | 0.050134
0.23931 | 3.5471e-07 | 0.99091 | 28068.7481 | 0.91649 | 0.93457 | 0.0066855 |  | 0.13905 | 2.1457e-08 | 0.98278 | 67034.0856 | 0.2644 | 0.88632 | 0.00085109 | 0.88027 | 2.0838e-06 | 0.56486 | 45372.3644 | 0.33261 | 0.91125 | 0.059278 |  | 0.066814
0.36072 | 4.8135e-07 | 0.39765 | 16615.9007 | 0.87603 | 0.92602 | 0.0068225 |  | 0.76583 | 1.2174e-07 | 0.22933 | 37865.1958 | 0.3872 | 0.90272 | 0.0031181 | 0.23655 | 8.064e-07 | 0.27501 | 38966.3926 | 0.50112 | 0.93036 | 0.019536 |  | 0.029477
0.99414 | 2.759e-06 | 0.87458 | 22019.084 | 0.16759 | 0.81217 | 0.070066 |  | 0.38111 | 5.0852e-08 | 0.98085 | 66458.6744 | 0.017773 | 0.80001 | 0.0022427 | 0.87012 | 2.04e-06 | 0.88171 | 55643.5089 | 0.7064 | 0.95018 | 0.062832 |  | 0.13514
0.68638 | 9.0426e-07 | 0.32156 | 15951.8988 | 0.0044723 | 0.68658 | 0.029779 |  | 0.57 | 7.8789e-08 | 0.21814 | 37582.7916 | 0.41042 | 0.90544 | 0.0019932 | 0.15015 | 6.6534e-07 | 0.84788 | 53931.7973 | 0.32775 | 0.91061 | 0.021548 |  | 0.05332
0.41702 | 5.4252e-07 | 0.63712 | 18772.6328 | 0.080191 | 0.78132 | 0.014371 |  | 0.60002 | 8.4084e-08 | 0.32791 | 40169.5212 | 0.64502 | 0.93 | 0.0020862 | 0.1694 | 6.9869e-07 | 0.89349 | 56334.5529 | 0.73799 | 0.95321 | 0.021623 |  | 0.038081
0.79849 | 1.1356e-06 | 0.37262 | 16399.6311 | 0.91842 | 0.93503 | 0.01517 |  | 0.38093 | 5.0828e-08 | 0.93186 | 59157.3432 | 0.36167 | 0.89961 | 0.0017995 | 0.99038 | 3.2937e-06 | 0.16228 | 36061.0947 | 0.66407 | 0.94617 | 0.071722 |  | 0.088691
0.28551 | 4.0253e-07 | 0.61635 | 18567.7065 | 0.00305 | 0.67587 | 0.013955 |  | 0.51063 | 6.9149e-08 | 0.44639 | 42746.5165 | 0.10591 | 0.85309 | 0.0021507 | 0.77355 | 1.7259e-06 | 0.98757 | 68782.2116 | 0.31211 | 0.90853 | 0.067756 |  | 0.083862
0.35788 | 4.7832e-07 | 0.56297 | 18064.4536 | 0.91115 | 0.93333 | 0.0068256 |  | 0.40996 | 5.4679e-08 | 0.11606 | 34579.4426 | 0.040782 | 0.82339 | 0.0016243 | 0.27063 | 8.5792e-07 | 0.17446 | 36412.3493 | 0.54403 | 0.93466 | 0.019509 |  | 0.027959
0.95747 | 1.8794e-06 | 0.51842 | 17663.1654 | 0.79687 | 0.91254 | 0.029545 |  | 0.39881 | 5.3185e-08 | 0.16639 | 36181.1373 | 0.77697 | 0.94359 | 0.0011707 | 0.3711 | 1.0052e-06 | 0.34531 | 40554.3586 | 0.72995 | 0.95243 | 0.023601 |  | 0.054317
0.26528 | 3.8159e-07 | 0.91178 | 22933.6726 | 0.30557 | 0.84167 | 0.0089753 |  | 0.81399 | 1.3736e-07 | 0.026413 | 29813.9958 | 0.059363 | 0.83464 | 0.0036987 | 0.91979 | 2.2929e-06 | 0.36958 | 41085.4419 | 0.15208 | 0.8806 | 0.065461 |  | 0.078135
0.83967 | 1.2503e-06 | 0.0016015 | 9705.8903 | 0.96051 | 0.94722 | 0.011528 |  | 0.10679 | 1.7525e-08 | 0.19489 | 36975.0752 | 0.78275 | 0.94422 | 0.00039155 | 0.76521 | 1.7043e-06 | 0.59309 | 46032.4075 | 0.64454 | 0.94432 | 0.045356 |  | 0.057276
0.57668 | 7.3708e-07 | 0.35425 | 16239.8605 | 0.39465 | 0.85623 | 0.014408 |  | 0.60704 | 8.537e-08 | 0.65209 | 47486.1369 | 0.41354 | 0.9058 | 0.0025405 | 0.25688 | 8.3731e-07 | 0.578 | 45677.3739 | 0.4239 | 0.92217 | 0.023344 |  | 0.040292
0.36234 | 4.8308e-07 | 0.98668 | 27264.1485 | 0.71746 | 0.90093 | 0.010125 |  | 0.90526 | 1.8193e-07 | 0.026685 | 29840.3627 | 0.33739 | 0.89654 | 0.0040824 | 0.65334 | 1.4593e-06 | 0.33589 | 40346.3971 | 0.080229 | 0.85859 | 0.043353 |  | 0.05756
0.24021 | 3.5565e-07 | 0.73048 | 19788.4331 | 0.13318 | 0.80206 | 0.008989 |  | 0.78282 | 1.2688e-07 | 0.85292 | 54165.9355 | 0.20586 | 0.87656 | 0.004384 | 0.37717 | 1.014e-06 | 0.84681 | 53883.0283 | 0.42466 | 0.92225 | 0.032102 |  | 0.045475
0.19587 | 3.0934e-07 | 0.0044986 | 10379.2949 | 0.27468 | 0.83603 | 0.0057855 |  | 0.85521 | 1.5409e-07 | 0.20325 | 37197.2365 | 0.068337 | 0.83899 | 0.0045776 | 0.84516 | 1.9438e-06 | 0.31174 | 39807.6381 | 0.10939 | 0.86901 | 0.055926 |  | 0.066289
0.76776 | 1.0629e-06 | 0.072134 | 13068.8121 | 0.48882 | 0.8699 | 0.018155 |  | 0.69646 | 1.0377e-07 | 0.52311 | 44426.5568 | 0.73496 | 0.93913 | 0.002718 | 0.70193 | 1.5573e-06 | 0.62315 | 46758.6295 | 0.064422 | 0.85146 | 0.051265 |  | 0.072138
0.13437 | 2.4255e-07 | 0.41041 | 16725.73 | 0.65506 | 0.89238 | 0.0040967 |  | 0.72631 | 1.1099e-07 | 0.52679 | 44508.836 | 0.60827 | 0.92632 | 0.0030044 | 0.86466 | 2.0177e-06 | 0.86906 | 54961.8896 | 0.16735 | 0.88408 | 0.069509 |  | 0.07661
0.95764 | 1.8813e-06 | 0.18112 | 14585.4319 | 0.24398 | 0.82999 | 0.039405 |  | 0.2088 | 2.9724e-08 | 0.29094 | 39335.0995 | 0.53244 | 0.91864 | 0.00074888 | 0.68115 | 1.5141e-06 | 0.51232 | 44186.6872 | 0.47651 | 0.92783 | 0.040611 |  | 0.080765
0.71974 | 9.6448e-07 | 0.02745 | 11921.0981 | 0.55569 | 0.87905 | 0.015272 |  | 0.65414 | 9.4544e-08 | 0.16234 | 36063.1396 | 0.6251 | 0.92801 | 0.0021783 | 0.96575 | 2.7113e-06 | 0.50197 | 43957.9187 | 0.83854 | 0.9634 | 0.066103 |  | 0.083554
0.90267 | 1.493e-06 | 0.84437 | 21429.3192 | 0.56484 | 0.88028 | 0.02974 |  | 0.11549 | 1.8597e-08 | 0.57395 | 45582.8195 | 0.86899 | 0.95447 | 0.00047874 | 0.74598 | 1.6568e-06 | 0.79242 | 51687.4029 | 0.09897 | 0.8656 | 0.056569 |  | 0.086788
0.20193 | 3.1573e-07 | 0.47958 | 17322.4068 | 0.76647 | 0.90795 | 0.0050286 |  | 0.93815 | 2.0944e-07 | 0.046548 | 31386.8208 | 0.77963 | 0.94388 | 0.004132 | 0.51967 | 1.2285e-06 | 0.934 | 59352.6104 | 0.11494 | 0.87071 | 0.045658 |  | 0.054819
0.3011 | 4.1871e-07 | 0.012028 | 11145.0517 | 0.92914 | 0.93769 | 0.0044732 |  | 0.17177 | 2.5354e-08 | 0.69472 | 48623.1792 | 0.93773 | 0.96512 | 0.00067236 | 0.38749 | 1.0291e-06 | 0.25662 | 38531.7181 | 0.64042 | 0.94393 | 0.023769 |  | 0.028915
0.39445 | 5.1769e-07 | 0.57819 | 18204.9911 | 0.042533 | 0.7577 | 0.014559 |  | 0.5082 | 6.8774e-08 | 0.044335 | 31241.6786 | 0.62879 | 0.92838 | 0.0014289 | 0.66024 | 1.4726e-06 | 0.32645 | 40136.9787 | 0.71564 | 0.95106 | 0.03442 |  | 0.050408
0.41323 | 5.3832e-07 | 0.11684 | 13791.5655 | 0.58848 | 0.88345 | 0.0087754 |  | 0.59853 | 8.3813e-08 | 0.81945 | 52715.0406 | 0.95256 | 0.96816 | 0.0023725 | 0.78384 | 1.7534e-06 | 0.18871 | 36807.7829 | 0.39418 | 0.91879 | 0.042122 |  | 0.05327
0.11407 | 2.1919e-07 | 0.66272 | 19033.9307 | 0.96783 | 0.95008 | 0.0029403 |  | 0.55845 | 7.6832e-08 | 0.054971 | 31898.3527 | 0.81309 | 0.94762 | 0.0015138 | 0.83669 | 1.9141e-06 | 0.274 | 38942.6599 | 0.92974 | 0.97481 | 0.040556 |  | 0.04501
0.5875 | 7.5196e-07 | 0.89379 | 22457.7817 | 0.59913 | 0.88488 | 0.015055 |  | 0.62639 | 8.9018e-08 | 0.66702 | 47874.6626 | 0.75343 | 0.94107 | 0.0024648 | 0.35232 | 9.7782e-07 | 0.89476 | 56412.3918 | 0.2594 | 0.9009 | 0.033336 |  | 0.050856
0.54333 | 6.9285e-07 | 0.2971 | 15731.9149 | 0.34955 | 0.84912 | 0.013785 |  | 0.86534 | 1.5889e-07 | 0.79564 | 51804.4089 | 0.47901 | 0.91304 | 0.004968 | 0.31275 | 9.2012e-07 | 0.31149 | 39801.9631 | 0.61058 | 0.9411 | 0.02198 |  | 0.040733
0.28856 | 4.0569e-07 | 0.80529 | 20787.9923 | 0.46249 | 0.8662 | 0.0084077 |  | 0.3377 | 4.5296e-08 | 0.94182 | 60117.2571 | 0.10473 | 0.85272 | 0.0017454 | 0.67951 | 1.5108e-06 | 0.26014 | 38615.7892 | 0.73619 | 0.95304 | 0.034016 |  | 0.044169
0.29578 | 4.1318e-07 | 0.089103 | 13369.6174 | 0.8314 | 0.91808 | 0.0055009 |  | 0.63955 | 9.1592e-08 | 0.45844 | 43007.4635 | 0.90028 | 0.95885 | 0.0022187 | 0.86468 | 2.0178e-06 | 0.91387 | 57698.791 | 0.52802 | 0.93307 | 0.066145 |  | 0.073865
0.45294 | 5.8308e-07 | 0.95567 | 24600.1766 | 0.92769 | 0.93732 | 0.009924 |  | 0.59722 | 8.3577e-08 | 0.77539 | 51089.9456 | 0.9355 | 0.9647 | 0.0023181 | 0.28729 | 8.8267e-07 | 0.66094 | 47715.3569 | 0.97195 | 0.98265 | 0.022035 |  | 0.034277
0.67165 | 8.7933e-07 | 0.21074 | 14901.6389 | 0.8459 | 0.92054 | 0.012152 |  | 0.18142 | 2.6495e-08 | 0.5238 | 44441.9887 | 0.084893 | 0.84586 | 0.00085574 | 0.23898 | 8.1013e-07 | 0.78103 | 51284.1485 | 0.063524 | 0.85101 | 0.028252 |  | 0.041259
0.33763 | 4.5689e-07 | 0.19082 | 14691.52 | 0.035436 | 0.75128 | 0.012476 |  | 0.55598 | 7.642e-08 | 0.44329 | 42679.4984 | 0.0061444 | 0.77245 | 0.002783 | 0.17338 | 7.0542e-07 | 0.044086 | 31225.0499 | 0.33709 | 0.91183 | 0.015491 |  | 0.03075
0.63815 | 8.2586e-07 | 0.39577 | 16599.67 | 0.44168 | 0.86321 | 0.015813 |  | 0.94005 | 2.1144e-07 | 0.78865 | 51552.1285 | 0.49927 | 0.91519 | 0.0065588 | 0.45867 | 1.1345e-06 | 0.69625 | 48665.607 | 0.73531 | 0.95295 | 0.030982 |  | 0.053353
0.45541 | 5.8593e-07 | 0.78076 | 20433.9599 | 0.87658 | 0.92613 | 0.0093358 |  | 0.75505 | 1.1865e-07 | 0.033913 | 30478.2264 | 0.74263 | 0.93993 | 0.0023239 | 0.16797 | 6.9625e-07 | 0.88125 | 55617.603 | 0.70912 | 0.95044 | 0.021425 |  | 0.033085
0.65972 | 8.5981e-07 | 0.23828 | 15178.4768 | 0.35926 | 0.85069 | 0.016797 |  | 0.67507 | 9.8973e-08 | 0.012614 | 28069.0492 | 0.90785 | 0.96001 | 0.0016802 | 0.074832 | 5.1231e-07 | 0.24274 | 38196.526 | 0.77269 | 0.9566 | 0.011307 |  | 0.029784
0.44708 | 5.7636e-07 | 0.46991 | 17238.4987 | 0.67649 | 0.89529 | 0.0097345 |  | 0.24289 | 3.3759e-08 | 0.76231 | 50652.9261 | 0.26227 | 0.88599 | 0.0010947 | 0.29425 | 8.9295e-07 | 0.045163 | 31296.5708 | 0.2438 | 0.89842 | 0.0205 |  | 0.031329
0.44912 | 5.787e-07 | 0.23356 | 15131.9777 | 0.093868 | 0.78756 | 0.014218 |  | 0.96219 | 2.4075e-07 | 0.16645 | 36182.8316 | 0.49846 | 0.91511 | 0.0057761 | 0.26544 | 8.5016e-07 | 0.91893 | 58080.1883 | 0.49594 | 0.92984 | 0.028182 |  | 0.048176
0.70223 | 9.3217e-07 | 0.77457 | 20349.1682 | 0.19085 | 0.81814 | 0.02261 |  | 0.85574 | 1.5433e-07 | 0.16231 | 36062.2189 | 0.5978 | 0.92527 | 0.0035851 | 0.94538 | 2.4855e-06 | 0.41942 | 42164.0409 | 0.14872 | 0.87979 | 0.072274 |  | 0.098469
0.50874 | 6.4931e-07 | 0.021978 | 11697.1301 | 0.2284 | 0.82672 | 0.012995 |  | 0.51189 | 6.9344e-08 | 0.72752 | 49566.3265 | 0.31249 | 0.89324 | 0.0021836 | 0.3871 | 1.0285e-06 | 0.31978 | 39988.1273 | 0.081951 | 0.85929 | 0.030348 |  | 0.045527
0.41295 | 5.3801e-07 | 0.0076491 | 10774.6481 | 0.54377 | 0.87744 | 0.0083195 |  | 0.23921 | 3.3322e-08 | 0.70814 | 49000.6806 | 0.014819 | 0.79513 | 0.0012471 | 0.038821 | 4.0962e-07 | 0.062785 | 32326.3588 | 0.45658 | 0.92572 | 0.0087942 |  | 0.018361
0.0349 | 1.1063e-07 | 0.58685 | 18285.9822 | 0.74551 | 0.90491 | 0.0018369 |  | 0.78156 | 1.2648e-07 | 0.63535 | 47061.4236 | 0.56215 | 0.92168 | 0.0036109 | 0.71394 | 1.5833e-06 | 0.11839 | 34661.6868 | 0.55628 | 0.93586 | 0.034576 |  | 0.040023
0.65168 | 8.4697e-07 | 0.20517 | 14843.8673 | 0.38707 | 0.85506 | 0.016128 |  | 0.0061092 | 2.3442e-09 | 0.68288 | 48298.3881 | 0.49683 | 0.91493 | 6.9264e-05 | 0.89084 | 2.1329e-06 | 0.4413 | 42636.4012 | 0.35226 | 0.91375 | 0.057664 |  | 0.073862
0.1407 | 2.4966e-07 | 0.96129 | 24913.9259 | 0.29035 | 0.83894 | 0.0061314 |  | 0.99709 | 3.9954e-07 | 0.067558 | 32570.22 | 0.28405 | 0.88924 | 0.0096623 | 0.21657 | 7.7542e-07 | 0.36164 | 40912.2602 | 0.72491 | 0.95195 | 0.018364 |  | 0.034157
0.038281 | 1.1644e-07 | 0.78359 | 20473.2633 | 0.39524 | 0.85632 | 0.0024863 |  | 0.72923 | 1.1173e-07 | 0.060725 | 32217.2114 | 0.61368 | 0.92687 | 0.0023841 | 0.060117 | 4.7455e-07 | 0.77377 | 51034.8312 | 0.791 | 0.95843 | 0.013334 |  | 0.018204
0.36739 | 4.8847e-07 | 0.27661 | 15543.7567 | 0.45634 | 0.86532 | 0.0090479 |  | 0.97712 | 2.7235e-07 | 0.31759 | 39939.1255 | 0.33624 | 0.89639 | 0.007347 | 0.10486 | 5.7921e-07 | 0.59473 | 46071.3786 | 0.24837 | 0.89916 | 0.017114 |  | 0.033509
0.31285 | 4.3094e-07 | 0.14536 | 14167.2324 | 0.11631 | 0.79633 | 0.010119 |  | 0.14988 | 2.2753e-08 | 0.20735 | 37304.4463 | 0.78568 | 0.94454 | 0.0005114 | 0.89746 | 2.1659e-06 | 0.6002 | 46201.832 | 0.8871 | 0.96901 | 0.054363 |  | 0.064993
0.25878 | 3.7487e-07 | 0.12775 | 13940.9192 | 0.076172 | 0.77932 | 0.0092831 |  | 0.084976 | 1.477e-08 | 0.78711 | 51497.4139 | 0.043437 | 0.82525 | 0.00053994 | 0.45868 | 1.1345e-06 | 0.16926 | 36263.8822 | 0.1959 | 0.88995 | 0.029243 |  | 0.039066
0.79035 | 1.1154e-06 | 0.76808 | 20262.1045 | 0.26481 | 0.83414 | 0.025632 |  | 0.18301 | 2.6682e-08 | 0.73072 | 49662.1574 | 0.88361 | 0.95645 | 0.0007355 | 0.83249 | 1.8999e-06 | 0.4438 | 42690.5778 | 0.30236 | 0.90719 | 0.052236 |  | 0.078604
0.027341 | 9.6764e-08 | 0.40341 | 16665.4676 | 0.51993 | 0.8742 | 0.0017713 |  | 0.16099 | 2.4075e-08 | 0.97188 | 64332.7943 | 0.8729 | 0.95498 | 0.00083449 | 0.82048 | 1.8608e-06 | 0.33895 | 40414.0719 | 0.041535 | 0.83771 | 0.057953 |  | 0.060559
0.68895 | 9.087e-07 | 0.085967 | 13317.0069 | 0.44921 | 0.8643 | 0.016032 |  | 0.28773 | 3.9136e-08 | 0.67592 | 48110.9759 | 0.63858 | 0.92936 | 0.0011171 | 0.28043 | 8.7251e-07 | 0.41755 | 42123.782 | 0.3022 | 0.90717 | 0.023766 |  | 0.040915
0.22512 | 3.3997e-07 | 0.51962 | 17673.784 | 0.38885 | 0.85534 | 0.0068778 |  | 0.44848 | 5.9987e-08 | 0.57333 | 45568.4695 | 0.86201 | 0.95355 | 0.0015474 | 0.9711 | 2.7916e-06 | 0.42428 | 42269.025 | 0.81725 | 0.96113 | 0.066212 |  | 0.074637
0.27046 | 3.8695e-07 | 0.27905 | 15566.3406 | 0.88275 | 0.92733 | 0.0052561 |  | 0.72361 | 1.1031e-07 | 0.56953 | 45480.2952 | 0.63971 | 0.92947 | 0.0030131 | 0.081639 | 5.2848e-07 | 0.55742 | 45201.6312 | 0.77977 | 0.95731 | 0.013411 |  | 0.02168
0.32143 | 4.399e-07 | 0.74185 | 19926.6747 | 0.37278 | 0.85284 | 0.0094086 |  | 0.30072 | 4.0717e-08 | 0.6148 | 46553.9872 | 0.22676 | 0.88025 | 0.0012614 | 0.51977 | 1.2287e-06 | 0.75933 | 50555.6301 | 0.015289 | 0.8084 | 0.04573 |  | 0.0564
0.91374 | 1.5505e-06 | 0.56127 | 18048.8727 | 0.58114 | 0.88247 | 0.028311 |  | 0.69775 | 1.0407e-07 | 0.4113 | 41988.9361 | 0.1174 | 0.85654 | 0.0031792 | 0.26686 | 8.5229e-07 | 0.0037247 | 25713.9561 | 0.82655 | 0.96211 | 0.013371 |  | 0.044861
0.025456 | 9.3075e-08 | 0.65354 | 18939.0371 | 0.45964 | 0.86579 | 0.0018573 |  | 0.34351 | 4.6028e-08 | 0.8544 | 54236.0534 | 0.18515 | 0.8726 | 0.0016028 | 0.45099 | 1.1229e-06 | 0.52329 | 44430.6058 | 0.43238 | 0.9231 | 0.030592 |  | 0.034052
0.42523 | 5.5167e-07 | 0.16181 | 14365.6149 | 0.2309 | 0.82726 | 0.011626 |  | 0.19785 | 2.8432e-08 | 0.77897 | 51212.5887 | 0.65379 | 0.93088 | 0.00084988 | 0.28631 | 8.8123e-07 | 0.46108 | 43064.6711 | 0.27891 | 0.90384 | 0.024573 |  | 0.037049
0.40497 | 5.2921e-07 | 0.55348 | 17977.7653 | 0.0044682 | 0.68655 | 0.017797 |  | 0.68058 | 1.0018e-07 | 0.77475 | 51068.1349 | 0.65337 | 0.93084 | 0.0029881 | 0.47453 | 1.1585e-06 | 0.68184 | 48270.3039 | 0.34878 | 0.91331 | 0.034334 |  | 0.055119
0.42566 | 5.5215e-07 | 0.098541 | 13521.2534 | 0.32923 | 0.84575 | 0.010618 |  | 0.16873 | 2.4993e-08 | 0.36286 | 40938.876 | 0.79975 | 0.9461 | 0.00060202 | 0.20322 | 7.5428e-07 | 0.1619 | 36050.0661 | 0.81463 | 0.96086 | 0.01565 |  | 0.02687
0.42787 | 5.5463e-07 | 0.73516 | 19844.8018 | 0.63021 | 0.88904 | 0.010284 |  | 0.96714 | 2.4962e-07 | 0.17307 | 36372.7654 | 0.69929 | 0.93547 | 0.0056578 | 0.5923 | 1.3484e-06 | 0.19099 | 36869.7583 | 0.86869 | 0.9668 | 0.027954 |  | 0.043896
0.7897 | 1.1138e-06 | 0.63037 | 18705.3632 | 0.61456 | 0.88695 | 0.02027 |  | 0.32041 | 4.314e-08 | 0.74707 | 50164.4115 | 0.48865 | 0.91407 | 0.0013138 | 0.68837 | 1.5289e-06 | 0.49579 | 43821.9761 | 0.44034 | 0.92397 | 0.041135 |  | 0.062719
0.58056 | 7.4237e-07 | 0.037098 | 12245.5689 | 0.31981 | 0.84415 | 0.013972 |  | 0.075117 | 1.3486e-08 | 0.38338 | 41385.1919 | 0.012656 | 0.79095 | 0.00046767 | 0.344 | 9.6571e-07 | 0.059893 | 32172.4431 | 0.37799 | 0.91689 | 0.021275 |  | 0.035715
0.75286 | 1.0306e-06 | 0.35224 | 16222.3706 | 0.091464 | 0.78652 | 0.025848 |  | 0.8144 | 1.3751e-07 | 0.8485 | 53960.415 | 0.2566 | 0.88512 | 0.0046676 | 0.99918 | 4.3433e-06 | 0.99868 | 80142.04 | 0.96608 | 0.9813 | 0.1779 |  | 0.20842
0.97215 | 2.0716e-06 | 0.74702 | 19990.8571 | 0.79454 | 0.91218 | 0.034825 |  | 0.12435 | 1.9681e-08 | 0.99303 | 71811.5709 | 0.75915 | 0.94167 | 0.00076599 | 0.52544 | 1.2377e-06 | 0.35559 | 40780.0256 | 0.75147 | 0.95452 | 0.02902 |  | 0.064611
0.48537 | 6.2104e-07 | 0.88517 | 22253.2805 | 0.0029488 | 0.67494 | 0.022348 |  | 0.35281 | 4.7205e-08 | 0.22682 | 37802.4442 | 0.18423 | 0.87242 | 0.001306 | 0.2344 | 8.0311e-07 | 0.85047 | 54051.4228 | 0.78682 | 0.95801 | 0.023747 |  | 0.047401
0.45983 | 5.9103e-07 | 0.39235 | 16570.1417 | 0.26569 | 0.83431 | 0.012664 |  | 0.4281 | 5.7147e-08 | 0.86111 | 54560.3912 | 0.029299 | 0.81386 | 0.0022006 | 0.87876 | 2.0771e-06 | 0.027342 | 29903.3001 | 0.91503 | 0.97267 | 0.03518 |  | 0.050044
0.14352 | 2.528e-07 | 0.73955 | 19898.3661 | 0.19918 | 0.82014 | 0.0060458 |  | 0.67175 | 9.8256e-08 | 0.70226 | 48834.1223 | 0.80285 | 0.94645 | 0.0027315 | 0.63234 | 1.4198e-06 | 0.33563 | 40340.6512 | 0.425 | 0.92229 | 0.036079 |  | 0.044856
0.61851 | 7.9631e-07 | 0.040721 | 12351.3809 | 0.49143 | 0.87027 | 0.01333 |  | 0.5596 | 7.7027e-08 | 0.89609 | 56495.29 | 0.13902 | 0.86234 | 0.0028052 | 0.088183 | 5.4341e-07 | 0.075672 | 32959.6464 | 0.10351 | 0.86712 | 0.014091 |  | 0.030225
0.82644 | 1.2108e-06 | 0.77532 | 20359.3983 | 0.65309 | 0.89212 | 0.022439 |  | 0.89906 | 1.778e-07 | 0.68141 | 48258.7071 | 0.58596 | 0.92408 | 0.0051469 | 0.75295 | 1.6737e-06 | 0.94165 | 60099.0173 | 0.5638 | 0.9366 | 0.056401 |  | 0.083986
0.92902 | 1.6423e-06 | 0.90333 | 22700.7581 | 0.19172 | 0.81835 | 0.041389 |  | 0.79783 | 1.3174e-07 | 0.061934 | 32281.5773 | 0.79642 | 0.94573 | 0.0026372 | 0.6688 | 1.4894e-06 | 0.94822 | 60813.7345 | 0.91664 | 0.97289 | 0.047597 |  | 0.091623
0.27523 | 3.9189e-07 | 0.21451 | 14940.4552 | 0.58966 | 0.88361 | 0.0065822 |  | 0.84943 | 1.5149e-07 | 0.29791 | 39494.5331 | 0.78641 | 0.94462 | 0.0035608 | 0.47207 | 1.1547e-06 | 0.80351 | 52096.1767 | 0.95973 | 0.97998 | 0.031502 |  | 0.041645
0.1503 | 2.6032e-07 | 0.4407 | 16986.2849 | 0.33031 | 0.84594 | 0.0053835 |  | 0.97623 | 2.6995e-07 | 0.85271 | 54155.9779 | 0.95243 | 0.96813 | 0.0078303 | 0.93635 | 2.4096e-06 | 0.95511 | 61655.7408 | 0.21107 | 0.89279 | 0.08895 |  | 0.10216
0.84584 | 1.2698e-06 | 0.29984 | 15756.8149 | 0.99969 | 0.98342 | 0.011682 |  | 0.76418 | 1.2126e-07 | 0.97302 | 64564.9816 | 0.53723 | 0.91914 | 0.0044568 | 0.086592 | 5.3983e-07 | 0.045978 | 31349.8637 | 0.15936 | 0.88229 | 0.013032 |  | 0.02917
0.81304 | 1.1735e-06 | 0.64494 | 18851.3231 | 0.10627 | 0.79259 | 0.030088 |  | 0.56656 | 7.8203e-08 | 0.15015 | 35697.8665 | 0.42309 | 0.90689 | 0.0019037 | 0.69309 | 1.5387e-06 | 0.43832 | 42572.0972 | 0.61558 | 0.94157 | 0.038715 |  | 0.070706
0.37815 | 5.0002e-07 | 0.12017 | 13837.9504 | 0.13 | 0.80103 | 0.011487 |  | 0.84316 | 1.4877e-07 | 0.90301 | 56941.2239 | 0.92863 | 0.96345 | 0.0045573 | 0.61741 | 1.3927e-06 | 0.32644 | 40136.6232 | 0.69806 | 0.94939 | 0.032708 |  | 0.048752
0.93481 | 1.6822e-06 | 0.044892 | 12465.144 | 0.78718 | 0.91106 | 0.022658 |  | 0.6107 | 8.6048e-08 | 0.95834 | 62090.9911 | 0.97774 | 0.97499 | 0.0027931 | 0.63262 | 1.4204e-06 | 0.78682 | 51487.051 | 0.60382 | 0.94045 | 0.041797 |  | 0.067248
0.38543 | 5.0789e-07 | 0.50118 | 17511.1023 | 0.85928 | 0.92291 | 0.0075339 |  | 0.33296 | 4.4703e-08 | 0.61636 | 46592.0155 | 0.17583 | 0.87071 | 0.0014131 | 0.30844 | 9.138e-07 | 0.018202 | 28897.8147 | 0.34287 | 0.91257 | 0.019048 |  | 0.027995
0.89749 | 1.4683e-06 | 0.8375 | 21308.2722 | 0.52392 | 0.87474 | 0.029794 |  | 0.45795 | 6.1332e-08 | 0.71292 | 49138.0864 | 0.8035 | 0.94653 | 0.0017136 | 0.6536 | 1.4598e-06 | 0.27206 | 38897.3594 | 0.79253 | 0.95859 | 0.032511 |  | 0.064019
0.78533 | 1.1033e-06 | 0.085234 | 13304.5337 | 0.0050672 | 0.69014 | 0.035013 |  | 0.23838 | 3.3222e-08 | 0.93397 | 59349.6067 | 0.30879 | 0.89273 | 0.0011923 | 0.31477 | 9.2307e-07 | 0.39175 | 41566.3341 | 0.97767 | 0.98412 | 0.020163 |  | 0.056369
0.81049 | 1.1667e-06 | 0.91894 | 23146.4694 | 0.49807 | 0.87119 | 0.024927 |  | 0.68459 | 1.0107e-07 | 0.68057 | 48235.8658 | 0.36752 | 0.90034 | 0.0030771 | 0.53498 | 1.253e-06 | 0.042364 | 31108.0935 | 0.70577 | 0.95012 | 0.023991 |  | 0.051995
0.64732 | 8.401e-07 | 0.79927 | 20698.2768 | 0.87877 | 0.92655 | 0.013461 |  | 0.66573 | 9.6967e-08 | 0.033416 | 30437.7966 | 0.74442 | 0.94012 | 0.001896 | 0.054023 | 4.5748e-07 | 0.95031 | 61057.1824 | 0.90288 | 0.97102 | 0.014723 |  | 0.03008
0.36683 | 4.8787e-07 | 0.14161 | 14120.4096 | 0.74036 | 0.90417 | 0.0072099 |  | 0.47441 | 6.3711e-08 | 0.097538 | 33889.434 | 0.20005 | 0.87548 | 0.0016401 | 0.62003 | 1.3974e-06 | 0.56136 | 45291.8894 | 0.89495 | 0.96999 | 0.034368 |  | 0.043218
0.92525 | 1.618e-06 | 0.73997 | 19903.5027 | 0.14878 | 0.80687 | 0.040367 |  | 0.049888 | 1.0025e-08 | 0.73929 | 49922.6398 | 0.30543 | 0.89227 | 0.00031789 | 0.42294 | 1.0812e-06 | 0.94599 | 60562.177 | 0.62478 | 0.94245 | 0.036306 |  | 0.07699
0.013261 | 6.5609e-08 | 0.34466 | 16155.935 | 0.85716 | 0.92253 | 0.00093419 |  | 0.20633 | 2.9433e-08 | 0.35187 | 40698.517 | 0.29867 | 0.89133 | 0.00081405 | 0.53783 | 1.2575e-06 | 0.55411 | 45125.7625 | 0.80316 | 0.95967 | 0.031672 |  | 0.03342
0.096111 | 1.976e-07 | 0.20579 | 14850.3323 | 0.44766 | 0.86408 | 0.0036206 |  | 0.72051 | 1.0953e-07 | 0.75529 | 50425.1391 | 0.79137 | 0.94517 | 0.0031364 | 0.0070693 | 2.4241e-07 | 0.40573 | 41868.5641 | 0.012814 | 0.80346 | 0.0082507 |  | 0.015008
0.83847 | 1.2466e-06 | 0.23345 | 15130.8547 | 0.71233 | 0.90022 | 0.019387 |  | 0.06341 | 1.1917e-08 | 0.38631 | 41448.6815 | 0.98431 | 0.97752 | 0.00026488 | 0.90672 | 2.2152e-06 | 0.34333 | 40510.7438 | 0.79692 | 0.95903 | 0.050982 |  | 0.070633
0.91564 | 1.561e-06 | 0.26199 | 15406.6449 | 0.93503 | 0.93925 | 0.019601 |  | 0.67605 | 9.9188e-08 | 0.93469 | 59416.7303 | 0.50704 | 0.91601 | 0.003429 | 0.32054 | 9.315e-07 | 0.36506 | 40986.8017 | 0.26883 | 0.90234 | 0.025194 |  | 0.048225
0.0078246 | 4.9708e-08 | 0.9316 | 23566.1552 | 0.85816 | 0.92271 | 0.00087701 |  | 0.95556 | 2.3051e-07 | 0.91973 | 58142.4586 | 0.49855 | 0.91511 | 0.0078465 | 0.19735 | 7.4485e-07 | 0.47358 | 43336.3302 | 0.94014 | 0.97645 | 0.017296 |  | 0.02602
0.117 | 2.2262e-07 | 0.22719 | 15068.6446 | 0.98058 | 0.9563 | 0.0024562 |  | 0.86237 | 1.5745e-07 | 0.60887 | 46410.1832 | 0.078459 | 0.84334 | 0.0052419 | 0.5561 | 1.2873e-06 | 0.12827 | 34999.2126 | 0.019201 | 0.81487 | 0.039234 |  | 0.046933
0.98294 | 2.2905e-06 | 0.067255 | 12973.8348 | 0.24729 | 0.83066 | 0.04632 |  | 0.81167 | 1.3652e-07 | 0.10253 | 34082.7665 | 0.30964 | 0.89285 | 0.0033587 | 0.20302 | 7.5396e-07 | 0.2164 | 37538.2344 | 0.0042601 | 0.77398 | 0.02588 |  | 0.075559
0.79657 | 1.1308e-06 | 0.23737 | 15169.4704 | 0.39159 | 0.85576 | 0.021627 |  | 0.23493 | 3.2814e-08 | 0.42551 | 42295.5789 | 0.11183 | 0.85491 | 0.0010103 | 0.48052 | 1.1676e-06 | 0.52238 | 44410.1974 | 0.8855 | 0.96881 | 0.028309 |  | 0.050946
0.97121 | 2.0565e-06 | 0.071632 | 13059.2445 | 0.73832 | 0.90388 | 0.029455 |  | 0.29467 | 3.9979e-08 | 0.7116 | 49099.9802 | 0.23193 | 0.88113 | 0.0012811 | 0.063826 | 4.8448e-07 | 0.94508 | 60462.7391 | 0.18628 | 0.88805 | 0.017758 |  | 0.048494
0.17974 | 2.9222e-07 | 0.30489 | 15802.4568 | 0.53624 | 0.87642 | 0.0051871 |  | 0.41373 | 5.5187e-08 | 0.32583 | 40123.1035 | 0.73413 | 0.93904 | 0.0013343 | 0.043267 | 4.2456e-07 | 0.38263 | 41368.9488 | 0.59881 | 0.93997 | 0.010487 |  | 0.017009
0.97918 | 2.2019e-06 | 0.55976 | 18035.0271 | 0.30382 | 0.84136 | 0.047306 |  | 0.23937 | 3.3341e-08 | 0.20698 | 37294.8781 | 0.40689 | 0.90503 | 0.00084005 | 0.7696 | 1.7156e-06 | 0.62262 | 46745.4942 | 0.034524 | 0.83209 | 0.0586 |  | 0.10675
0.56824 | 7.2565e-07 | 0.061462 | 12854.8462 | 0.93137 | 0.93827 | 0.0082999 |  | 0.72178 | 1.0985e-07 | 0.14755 | 35617.7925 | 0.93888 | 0.96534 | 0.0022221 | 0.3989 | 1.0458e-06 | 0.82623 | 52990.9602 | 0.67189 | 0.94691 | 0.031101 |  | 0.041623
0.35993 | 4.805e-07 | 0.52722 | 17741.4481 | 0.74618 | 0.905 | 0.0078561 |  | 0.094136 | 1.5939e-08 | 0.13013 | 35061.1561 | 0.53646 | 0.91906 | 0.00036982 | 0.49341 | 1.1875e-06 | 0.57648 | 45641.9013 | 0.97451 | 0.98329 | 0.028385 |  | 0.03661
0.94835 | 1.7902e-06 | 0.7537 | 20075.1225 | 0.14026 | 0.8043 | 0.045143 |  | 0.3574 | 4.779e-08 | 0.1417 | 35435.1944 | 0.47483 | 0.91259 | 0.0011386 | 0.87918 | 2.0789e-06 | 0.23214 | 37935.1507 | 0.88445 | 0.96868 | 0.0439 |  | 0.090182
0.56347 | 7.1927e-07 | 0.10296 | 13589.1518 | 0.2929 | 0.8394 | 0.014221 |  | 0.19554 | 2.8161e-08 | 0.48163 | 43511.8052 | 0.74265 | 0.93993 | 0.00072404 | 0.17493 | 7.0801e-07 | 0.99748 | 76956.3112 | 0.63697 | 0.94361 | 0.029204 |  | 0.04415
0.80248 | 1.1457e-06 | 0.02671 | 11892.9002 | 0.56267 | 0.87999 | 0.01804 |  | 0.58031 | 8.0572e-08 | 0.57439 | 45593.2018 | 0.55392 | 0.92084 | 0.0022501 | 0.53823 | 1.2582e-06 | 0.94938 | 60947.5901 | 0.51055 | 0.93132 | 0.043278 |  | 0.063568
0.32749 | 4.4624e-07 | 0.78706 | 20522.0252 | 0.33112 | 0.84607 | 0.0098913 |  | 0.42516 | 5.6743e-08 | 0.21652 | 37541.4694 | 0.26682 | 0.88669 | 0.0015077 | 0.35961 | 9.8843e-07 | 0.25356 | 38458.4677 | 0.11243 | 0.86995 | 0.027795 |  | 0.039194
0.51515 | 6.5723e-07 | 0.11313 | 13738.9081 | 0.74368 | 0.90464 | 0.0095743 |  | 0.3279 | 4.4071e-08 | 0.18747 | 36774.0898 | 0.085938 | 0.84626 | 0.0012793 | 0.021847 | 3.4071e-07 | 0.90524 | 57090.8225 | 0.012424 | 0.8026 | 0.013697 |  | 0.024551
0.26228 | 3.7849e-07 | 0.52173 | 17692.5355 | 0.47131 | 0.86745 | 0.0072992 |  | 0.86855 | 1.6048e-07 | 0.29209 | 39361.5046 | 0.44631 | 0.90949 | 0.004145 | 0.67955 | 1.5109e-06 | 0.329 | 40193.6459 | 0.98418 | 0.98608 | 0.031784 |  | 0.043228
0.32148 | 4.3995e-07 | 0.81955 | 21009.4509 | 0.87376 | 0.92559 | 0.0071454 |  | 0.39653 | 5.2882e-08 | 0.21004 | 37374.4376 | 0.93531 | 0.96466 | 0.001117 | 0.80634 | 1.8174e-06 | 0.57015 | 45494.6362 | 0.96646 | 0.98139 | 0.043534 |  | 0.051797
0.86615 | 1.3392e-06 | 0.63123 | 18713.9004 | 0.024457 | 0.73866 | 0.039916 |  | 0.21758 | 3.0761e-08 | 0.93509 | 59453.985 | 0.63322 | 0.92882 | 0.0010412 | 0.88882 | 2.1232e-06 | 0.043137 | 31160.9866 | 0.87024 | 0.96698 | 0.03813 |  | 0.079087
0.71056 | 9.4734e-07 | 0.6638 | 19045.2382 | 0.11404 | 0.79551 | 0.024146 |  | 0.96256 | 2.4138e-07 | 0.36581 | 41003.1487 | 0.12812 | 0.85952 | 0.0072239 | 0.58096 | 1.329e-06 | 0.82826 | 53075.1268 | 0.23895 | 0.89762 | 0.043575 |  | 0.074945
0.040439 | 1.2005e-07 | 0.23926 | 15188.0796 | 0.89754 | 0.93035 | 0.0015806 |  | 0.78308 | 1.2696e-07 | 0.16647 | 36183.437 | 0.47742 | 0.91287 | 0.0030658 | 0.47153 | 1.1539e-06 | 0.24628 | 38282.6699 | 0.70011 | 0.94958 | 0.02607 |  | 0.030717
0.99007 | 2.529e-06 | 0.58654 | 18283.1015 | 0.25561 | 0.83234 | 0.056388 |  | 0.865 | 1.5872e-07 | 0.045984 | 31350.2731 | 0.89247 | 0.9577 | 0.0029709 | 0.8999 | 2.1785e-06 | 0.0002875 | 22056.6952 | 0.00028017 | 0.70861 | 0.072631 |  | 0.13199
0.9389 | 1.7123e-06 | 0.16187 | 14366.2535 | 0.31992 | 0.84417 | 0.033758 |  | 0.33064 | 4.4412e-08 | 0.068235 | 32603.8883 | 0.094969 | 0.8495 | 0.0012006 | 0.44736 | 1.1175e-06 | 0.38997 | 41527.9464 | 0.31841 | 0.90938 | 0.029972 |  | 0.06493
0.45674 | 5.8746e-07 | 0.37367 | 16408.7264 | 0.79365 | 0.91205 | 0.0089221 |  | 0.065814 | 1.2244e-08 | 0.63507 | 47054.4695 | 0.060375 | 0.83516 | 0.00041737 | 0.095156 | 5.5873e-07 | 0.018043 | 28877.2855 | 0.23751 | 0.89738 | 0.012262 |  | 0.021602
0.49856 | 6.369e-07 | 0.35205 | 16220.6894 | 0.96923 | 0.95067 | 0.0076628 |  | 0.57465 | 7.9589e-08 | 0.96316 | 62800.5719 | 0.28568 | 0.88948 | 0.0029934 | 0.98593 | 3.1231e-06 | 0.72551 | 49506.5209 | 0.98649 | 0.98689 | 0.07988 |  | 0.090536
0.42333 | 5.4955e-07 | 0.13354 | 14017.2018 | 0.87883 | 0.92656 | 0.007104 |  | 0.84025 | 1.4755e-07 | 0.69007 | 48494.6653 | 0.76473 | 0.94227 | 0.0041174 | 0.29254 | 8.9042e-07 | 0.26326 | 38689.9287 | 0.61709 | 0.94172 | 0.020767 |  | 0.031989
0.53002 | 6.7585e-07 | 0.80886 | 20842.2675 | 0.063699 | 0.77249 | 0.01891 |  | 0.40457 | 5.3955e-08 | 0.48095 | 43497.0301 | 0.28678 | 0.88964 | 0.0015656 | 0.55545 | 1.2863e-06 | 0.50873 | 44107.1029 | 0.19645 | 0.89006 | 0.037636 |  | 0.058112
0.59654 | 7.6462e-07 | 0.49086 | 17420.7838 | 0.83387 | 0.91849 | 0.011577 |  | 0.25751 | 3.55e-08 | 0.31353 | 39848.0198 | 0.63861 | 0.92936 | 0.00087703 | 0.19468 | 7.4053e-07 | 0.93397 | 59350.0099 | 0.76893 | 0.95623 | 0.023853 |  | 0.036307
0.061384 | 1.5197e-07 | 0.45049 | 17070.6121 | 0.92302 | 0.93615 | 0.0020643 |  | 0.34392 | 4.6079e-08 | 0.70436 | 48893.2878 | 0.51757 | 0.9171 | 0.0013677 | 0.031086 | 3.8106e-07 | 0.69848 | 48727.7924 | 0.46942 | 0.92708 | 0.011041 |  | 0.014473
0.78569 | 1.1042e-06 | 0.55425 | 17984.8109 | 0.33737 | 0.84712 | 0.023199 |  | 0.83444 | 1.4517e-07 | 0.089567 | 33567.5587 | 0.061573 | 0.83576 | 0.0041248 | 0.58264 | 1.3318e-06 | 0.12519 | 34895.5987 | 0.91334 | 0.97243 | 0.025813 |  | 0.053136
0.23496 | 3.502e-07 | 0.1987 | 14775.7755 | 0.031651 | 0.74737 | 0.0096835 |  | 0.95283 | 2.2674e-07 | 0.75387 | 50379.7521 | 0.1782 | 0.87119 | 0.0075341 | 0.20762 | 7.6128e-07 | 0.53989 | 44803.1133 | 0.25253 | 0.89982 | 0.022026 |  | 0.039244
0.18181 | 2.9443e-07 | 0.49111 | 17422.9496 | 0.47125 | 0.86744 | 0.0056439 |  | 0.37602 | 5.019e-08 | 0.20313 | 37194.0717 | 0.65575 | 0.93108 | 0.0011721 | 0.83556 | 1.9103e-06 | 0.56766 | 45437.0872 | 0.80076 | 0.95943 | 0.048427 |  | 0.055243
0.95339 | 1.8374e-06 | 0.92706 | 23408.3896 | 0.39562 | 0.85638 | 0.041533 |  | 0.92799 | 1.9967e-07 | 0.036433 | 30676.9473 | 0.38453 | 0.9024 | 0.0044709 | 0.34178 | 9.6247e-07 | 0.18127 | 36603.2291 | 0.9848 | 0.98629 | 0.018529 |  | 0.064533
0.070399 | 1.6447e-07 | 0.22921 | 15088.7832 | 0.45976 | 0.86581 | 0.0030078 |  | 0.36814 | 4.9168e-08 | 0.87344 | 55191.2294 | 0.24704 | 0.88361 | 0.0017002 | 0.53347 | 1.2505e-06 | 0.010406 | 27659.4483 | 0.2156 | 0.89361 | 0.027109 |  | 0.031817
0.87645 | 1.3782e-06 | 0.76465 | 20216.7997 | 0.66162 | 0.89327 | 0.02533 |  | 0.94698 | 2.1929e-07 | 0.64309 | 47256.5028 | 0.34632 | 0.89769 | 0.0066168 | 0.52791 | 1.2416e-06 | 0.17318 | 36375.9948 | 0.090954 | 0.86276 | 0.034411 |  | 0.066358
0.80241 | 1.1455e-06 | 0.99736 | 30569.9692 | 0.65169 | 0.89193 | 0.026462 |  | 0.70245 | 1.0517e-07 | 0.32374 | 40076.4781 | 0.7746 | 0.94333 | 0.00251 | 0.62932 | 1.4143e-06 | 0.22415 | 37735.2317 | 0.57283 | 0.93747 | 0.032762 |  | 0.061734
0.41048 | 5.3528e-07 | 0.58749 | 18291.9483 | 0.96133 | 0.94752 | 0.0070995 |  | 0.49709 | 6.7082e-08 | 0.14069 | 35403.0005 | 0.0030909 | 0.75569 | 0.002333 | 0.53296 | 1.2497e-06 | 0.32932 | 40200.7384 | 0.57155 | 0.93735 | 0.030404 |  | 0.039837
0.99985 | 4.2927e-06 | 0.97196 | 25644.7075 | 0.74161 | 0.90435 | 0.085747 |  | 0.32255 | 4.3405e-08 | 0.48734 | 43636.6842 | 0.21543 | 0.87828 | 0.0012946 | 0.009592 | 2.6521e-07 | 0.070432 | 32711.5566 | 0.040607 | 0.83701 | 0.0074171 |  | 0.094459
0.72322 | 9.7111e-07 | 0.76471 | 20217.5127 | 0.23543 | 0.82822 | 0.022744 |  | 0.66993 | 9.7863e-08 | 0.057958 | 32066.5946 | 0.69095 | 0.93462 | 0.002027 | 0.41779 | 1.0736e-06 | 0.91769 | 57985.3704 | 0.032692 | 0.83045 | 0.041793 |  | 0.066564
0.36525 | 4.8618e-07 | 0.86431 | 21806.8969 | 0.63584 | 0.8898 | 0.0094102 |  | 0.014631 | 4.2522e-09 | 0.24077 | 38148.2555 | 0.065037 | 0.83746 | 0.00012847 | 0.87394 | 2.0561e-06 | 0.69025 | 48499.5997 | 0.89619 | 0.97015 | 0.053748 |  | 0.063287
0.62712 | 8.0912e-07 | 0.52591 | 17729.7151 | 0.82496 | 0.91701 | 0.01246 |  | 0.33483 | 4.4936e-08 | 0.70809 | 48999.4435 | 0.39608 | 0.90377 | 0.0013738 | 0.37909 | 1.0168e-06 | 0.46396 | 43127.2068 | 0.90675 | 0.97154 | 0.023838 |  | 0.037671
0.076764 | 1.7298e-07 | 0.32503 | 15982.732 | 0.77853 | 0.90975 | 0.0026253 |  | 0.091708 | 1.5631e-08 | 0.56056 | 45273.4743 | 0.37748 | 0.90155 | 0.0004538 | 0.40895 | 1.0605e-06 | 0.55826 | 45220.792 | 0.33688 | 0.9118 | 0.030058 |  | 0.033137
0.81912 | 1.1901e-06 | 0.68796 | 19303.0261 | 0.10495 | 0.79208 | 0.030774 |  | 0.66144 | 9.6061e-08 | 0.10681 | 34243.9796 | 0.10236 | 0.85196 | 0.002647 | 0.77701 | 1.735e-06 | 0.81828 | 52668.3046 | 0.0093348 | 0.79476 | 0.067507 |  | 0.10093
0.028027 | 9.8082e-08 | 0.54679 | 17917.1134 | 0.29157 | 0.83916 | 0.0021193 |  | 0.32081 | 4.319e-08 | 0.40923 | 41944.2708 | 0.92636 | 0.96305 | 0.0010121 | 0.61751 | 1.3928e-06 | 0.57373 | 45577.7227 | 0.7261 | 0.95207 | 0.036068 |  | 0.0392
0.16974 | 2.8149e-07 | 0.36566 | 16339.2956 | 0.34538 | 0.84844 | 0.0056884 |  | 0.091677 | 1.5627e-08 | 0.012631 | 28071.849 | 0.30606 | 0.89236 | 0.00034308 | 0.9015 | 2.1869e-06 | 0.37242 | 41147.237 | 0.6562 | 0.94543 | 0.052992 |  | 0.059023
0.7583 | 1.0422e-06 | 0.46119 | 17163.0701 | 0.86445 | 0.92385 | 0.015215 |  | 0.22919 | 3.2133e-08 | 0.61886 | 46653.2455 | 0.35253 | 0.89847 | 0.00095925 | 0.56246 | 1.2979e-06 | 0.17392 | 36396.9453 | 0.42703 | 0.92251 | 0.030598 |  | 0.046772
0.75674 | 1.0388e-06 | 0.22201 | 15016.6387 | 0.57965 | 0.88227 | 0.017595 |  | 0.38636 | 5.154e-08 | 0.75131 | 50298.1044 | 0.47325 | 0.91242 | 0.0015781 | 0.035299 | 3.9707e-07 | 0.42284 | 42237.8199 | 0.77491 | 0.95682 | 0.0095255 |  | 0.028699
0.42342 | 5.4965e-07 | 0.63513 | 18752.7375 | 0.61141 | 0.88652 | 0.010033 |  | 0.13068 | 2.0448e-08 | 0.17639 | 36466.7129 | 0.21452 | 0.87812 | 0.0005457 | 0.46279 | 1.1407e-06 | 0.86768 | 54890.649 | 0.85262 | 0.96496 | 0.033711 |  | 0.044289
0.2599 | 3.7603e-07 | 0.85119 | 21553.8914 | 0.18989 | 0.81791 | 0.0093128 |  | 0.6345 | 9.0595e-08 | 0.23195 | 37930.5915 | 0.015723 | 0.79671 | 0.0029822 | 0.19575 | 7.4228e-07 | 0.12036 | 34730.0104 | 0.33567 | 0.91164 | 0.017496 |  | 0.029791
0.34388 | 4.6348e-07 | 0.2671 | 15454.8758 | 0.52685 | 0.87514 | 0.0082037 |  | 0.5752 | 7.9684e-08 | 0.99856 | 79694.0463 | 0.72517 | 0.93812 | 0.0034106 | 0.70486 | 1.5636e-06 | 0.055217 | 31912.4264 | 0.78523 | 0.95785 | 0.029671 |  | 0.041285
0.54211 | 6.9129e-07 | 0.29432 | 15706.5927 | 0.53719 | 0.87655 | 0.012235 |  | 0.85945 | 1.5606e-07 | 0.54551 | 44930.1726 | 0.39858 | 0.90406 | 0.0044811 | 0.66782 | 1.4875e-06 | 0.0094246 | 27454.9102 | 0.22352 | 0.89501 | 0.031956 |  | 0.048672
0.74424 | 1.0127e-06 | 0.24561 | 15249.896 | 0.28269 | 0.83753 | 0.02088 |  | 0.30053 | 4.0694e-08 | 0.47409 | 43347.3176 | 0.73276 | 0.9389 | 0.0010459 | 0.21354 | 7.7065e-07 | 0.9266 | 58699.2074 | 0.16039 | 0.88253 | 0.027892 |  | 0.049818
0.55305 | 7.055e-07 | 0.098793 | 13525.1764 | 0.34281 | 0.84802 | 0.013439 |  | 0.91292 | 1.8739e-07 | 0.70378 | 48876.8099 | 0.90456 | 0.9595 | 0.005059 | 0.40531 | 1.0552e-06 | 0.43842 | 42574.2044 | 0.85453 | 0.96517 | 0.024899 |  | 0.043397
0.70063 | 9.293e-07 | 0.96196 | 24953.5036 | 0.71581 | 0.9007 | 0.018527 |  | 0.41888 | 5.5885e-08 | 0.64471 | 47297.697 | 0.74016 | 0.93967 | 0.0015372 | 0.26186 | 8.448e-07 | 0.43773 | 42559.4215 | 0.24915 | 0.89928 | 0.02362 |  | 0.043684
0.1717 | 2.836e-07 | 0.95645 | 24641.4248 | 0.58407 | 0.88286 | 0.005995 |  | 0.60039 | 8.4151e-08 | 0.37828 | 41274.4936 | 0.45366 | 0.91029 | 0.0022421 | 0.0047546 | 2.161e-07 | 0.90952 | 57386.4332 | 0.6578 | 0.94558 | 0.0068933 |  | 0.01513
0.37893 | 5.0087e-07 | 0.82471 | 21092.8929 | 0.43933 | 0.86287 | 0.010575 |  | 0.48976 | 6.598e-08 | 0.42723 | 42332.6365 | 0.43147 | 0.90783 | 0.0018005 | 0.31317 | 9.2072e-07 | 0.16877 | 36249.8222 | 0.19648 | 0.89006 | 0.02372 |  | 0.036095
0.40856 | 5.3316e-07 | 0.26108 | 15398.0623 | 0.9084 | 0.93271 | 0.0069713 |  | 0.06707 | 1.2413e-08 | 0.90476 | 57058.2211 | 0.46855 | 0.91192 | 0.00041872 | 0.46039 | 1.1371e-06 | 0.98097 | 66493.2202 | 0.83551 | 0.96307 | 0.040086 |  | 0.047476
0.17342 | 2.8546e-07 | 0.42633 | 16862.5875 | 0.92822 | 0.93745 | 0.0038203 |  | 0.67976 | 1e-07 | 0.064336 | 32406.9493 | 0.69251 | 0.93478 | 0.002086 | 0.65484 | 1.4622e-06 | 0.82066 | 52763.5082 | 0.0012225 | 0.74285 | 0.061593 |  | 0.067499
0.67348 | 8.8238e-07 | 0.22765 | 15073.3102 | 0.8172 | 0.91575 | 0.012602 |  | 0.2111 | 2.9996e-08 | 0.32065 | 40007.5699 | 0.89517 | 0.95809 | 0.000685 | 0.85879 | 1.9945e-06 | 0.064529 | 32416.89 | 0.89269 | 0.96971 | 0.036642 |  | 0.049929
0.56379 | 7.197e-07 | 0.6797 | 19213.5711 | 0.69182 | 0.89738 | 0.012674 |  | 0.13987 | 2.1555e-08 | 0.23679 | 38050.3017 | 0.015234 | 0.79587 | 0.00071181 | 0.29578 | 8.9519e-07 | 0.25665 | 38532.6605 | 0.13399 | 0.87607 | 0.024828 |  | 0.038214
0.059801 | 1.4971e-07 | 0.27693 | 15546.696 | 0.81546 | 0.91547 | 0.0021739 |  | 0.58625 | 8.1616e-08 | 0.61488 | 46556.0872 | 0.45079 | 0.90998 | 0.0023724 | 0.54971 | 1.2768e-06 | 0.88282 | 55705.7174 | 0.7178 | 0.95127 | 0.039281 |  | 0.043827
0.69875 | 9.2594e-07 | 0.44782 | 17047.6357 | 0.041057 | 0.75645 | 0.025725 |  | 0.8478 | 1.5078e-07 | 0.095126 | 33793.8146 | 0.89707 | 0.95837 | 0.0029914 | 0.6285 | 1.4128e-06 | 0.67552 | 48100.2476 | 0.63877 | 0.94378 | 0.039026 |  | 0.067743
0.90096 | 1.4847e-06 | 0.51373 | 17621.711 | 0.35988 | 0.85079 | 0.030536 |  | 0.024038 | 5.9926e-09 | 0.4007 | 41759.9208 | 0.9563 | 0.969 | 0.00013752 | 0.775 | 1.7297e-06 | 0.35999 | 40876.1351 | 0.32154 | 0.90979 | 0.045832 |  | 0.076505
0.73855 | 1.0012e-06 | 0.66213 | 19027.8075 | 0.59809 | 0.88474 | 0.018535 |  | 0.060096 | 1.1462e-08 | 0.28075 | 39099.897 | 0.09717 | 0.85025 | 0.0003409 | 0.71764 | 1.5915e-06 | 0.3138 | 39853.953 | 0.24019 | 0.89783 | 0.042717 |  | 0.061593
0.72366 | 9.7195e-07 | 0.17772 | 14547.6456 | 0.21718 | 0.82427 | 0.02079 |  | 0.14454 | 2.2115e-08 | 0.65921 | 47670.1253 | 0.57008 | 0.92248 | 0.00063644 | 0.91548 | 2.2662e-06 | 0.58281 | 45789.9283 | 0.64428 | 0.9443 | 0.060051 |  | 0.081477
0.94155 | 1.7329e-06 | 0.30667 | 15818.5402 | 0.66089 | 0.89317 | 0.028459 |  | 0.96525 | 2.4608e-07 | 0.55589 | 45166.5024 | 0.64272 | 0.92977 | 0.0066808 | 0.36471 | 9.9587e-07 | 0.51199 | 44179.2738 | 0.33672 | 0.91178 | 0.027754 |  | 0.062894
0.62213 | 8.0167e-07 | 0.30717 | 15823.0337 | 0.82677 | 0.91731 | 0.011625 |  | 0.34033 | 4.5627e-08 | 0.51028 | 44141.3942 | 0.35843 | 0.89921 | 0.0013084 | 0.59383 | 1.351e-06 | 0.30131 | 39571.9248 | 0.57146 | 0.93734 | 0.032473 |  | 0.045406
0.72689 | 9.7816e-07 | 0.05017 | 12598.8288 | 0.55608 | 0.8791 | 0.015776 |  | 0.24694 | 3.424e-08 | 0.1086 | 34310.087 | 0.4928 | 0.91451 | 0.00079361 | 0.84674 | 1.9495e-06 | 0.82586 | 52975.5648 | 0.40192 | 0.91968 | 0.061206 |  | 0.077776
0.92046 | 1.5888e-06 | 0.1728 | 14492.183 | 0.93464 | 0.93915 | 0.019281 |  | 0.53391 | 7.2811e-08 | 0.10521 | 34184.1102 | 0.76544 | 0.94235 | 0.0015405 | 0.70113 | 1.5556e-06 | 0.24996 | 38371.6908 | 0.39385 | 0.91875 | 0.038493 |  | 0.059315
0.32825 | 4.4704e-07 | 0.85424 | 21611.0443 | 0.61798 | 0.8874 | 0.0086959 |  | 0.0041835 | 1.8145e-09 | 0.27586 | 38986.1636 | 0.074962 | 0.8419 | 5.4909e-05 | 0.64298 | 1.4396e-06 | 0.33861 | 40406.583 | 0.96484 | 0.98103 | 0.030926 |  | 0.039676
0.67407 | 8.8337e-07 | 0.80996 | 20859.2553 | 0.23699 | 0.82854 | 0.020901 |  | 0.81331 | 1.3711e-07 | 0.44389 | 42692.3818 | 0.88707 | 0.95693 | 0.0033181 | 0.87523 | 2.0617e-06 | 0.037138 | 30730.7169 | 0.41367 | 0.92102 | 0.04344 |  | 0.06766
0.93366 | 1.674e-06 | 0.51995 | 17676.741 | 0.70496 | 0.89919 | 0.028086 |  | 0.70029 | 1.0466e-07 | 0.07421 | 32891.6261 | 0.27326 | 0.88766 | 0.0025578 | 0.68131 | 1.5145e-06 | 0.73542 | 49804.3294 | 0.041123 | 0.8374 | 0.053153 |  | 0.083797
0.11991 | 2.26e-07 | 0.45446 | 17104.91 | 0.98535 | 0.95934 | 0.0026594 |  | 0.76801 | 1.2238e-07 | 0.52077 | 44374.3143 | 0.12248 | 0.85798 | 0.0038521 | 0.56509 | 1.3022e-06 | 0.67781 | 48161.5933 | 0.42118 | 0.92186 | 0.037822 |  | 0.044333
0.93203 | 1.6626e-06 | 0.63359 | 18737.378 | 0.86479 | 0.92391 | 0.025473 |  | 0.21779 | 3.0786e-08 | 0.5314 | 44611.9681 | 0.020719 | 0.80419 | 0.0010803 | 0.91164 | 2.2432e-06 | 0.21867 | 37596.2388 | 0.71318 | 0.95083 | 0.049758 |  | 0.076311
0.77154 | 1.0713e-06 | 0.37979 | 16461.7417 | 0.33143 | 0.84612 | 0.021902 |  | 0.23911 | 3.3309e-08 | 0.62607 | 46830.5102 | 0.47962 | 0.91311 | 0.00096571 | 0.45082 | 1.1227e-06 | 0.41751 | 42122.8519 | 0.57998 | 0.93816 | 0.028264 |  | 0.051132
0.30592 | 4.2371e-07 | 0.63104 | 18712.0287 | 0.84262 | 0.91998 | 0.0066173 |  | 0.86551 | 1.5897e-07 | 0.58827 | 45918.4259 | 0.097753 | 0.85044 | 0.0051867 | 0.031903 | 3.8426e-07 | 0.36968 | 41087.537 | 0.54969 | 0.93522 | 0.0095633 |  | 0.021367
0.31011 | 4.2808e-07 | 0.79141 | 20583.8998 | 0.5149 | 0.87351 | 0.0085919 |  | 0.92563 | 1.976e-07 | 0.73206 | 49702.6768 | 0.85372 | 0.9525 | 0.0054995 | 0.19259 | 7.3714e-07 | 0.079828 | 33148.5634 | 0.11017 | 0.86926 | 0.019063 |  | 0.033154
0.91403 | 1.5521e-06 | 0.77675 | 20378.792 | 0.58536 | 0.88304 | 0.029868 |  | 0.1181 | 1.8917e-08 | 0.72508 | 49493.728 | 0.47607 | 0.91273 | 0.00057191 | 0.20438 | 7.5613e-07 | 0.48578 | 43602.4878 | 0.81089 | 0.96047 | 0.018451 |  | 0.048891
0.032209 | 1.0585e-07 | 0.68392 | 19259.1297 | 0.25753 | 0.83271 | 0.0023998 |  | 0.32518 | 4.3732e-08 | 0.10375 | 34129.199 | 0.3217 | 0.89448 | 0.0010718 | 0.97627 | 2.8837e-06 | 0.64736 | 47365.1725 | 0.55761 | 0.93599 | 0.080092 |  | 0.083564
0.8455 | 1.2687e-06 | 0.53776 | 17835.6746 | 0.64203 | 0.89063 | 0.022231 |  | 0.59724 | 8.358e-08 | 0.30741 | 39709.9139 | 0.25835 | 0.88539 | 0.0023084 | 0.54276 | 1.2655e-06 | 0.59722 | 46130.4768 | 0.91075 | 0.97208 | 0.03147 |  | 0.05601
0.20709 | 3.2114e-07 | 0.74083 | 19914.0991 | 0.51373 | 0.87335 | 0.0063557 |  | 0.16373 | 2.4401e-08 | 0.015322 | 28500.1961 | 0.98897 | 0.97977 | 0.00038392 | 0.53221 | 1.2485e-06 | 0.93259 | 59222.9927 | 0.13377 | 0.87602 | 0.045947 |  | 0.052686
0.75911 | 1.0439e-06 | 0.81558 | 20946.6148 | 0.77041 | 0.90854 | 0.018297 |  | 0.46457 | 6.2283e-08 | 0.79726 | 51863.5458 | 0.35049 | 0.89821 | 0.0020061 | 0.53366 | 1.2508e-06 | 0.25229 | 38427.9776 | 0.12308 | 0.87309 | 0.034889 |  | 0.055193
0.84306 | 1.2609e-06 | 0.025523 | 11846.4415 | 0.26559 | 0.83429 | 0.024535 |  | 0.92236 | 1.9482e-07 | 0.11889 | 34678.9045 | 0.79321 | 0.94537 | 0.0041258 | 0.33012 | 9.4549e-07 | 0.77078 | 50933.793 | 0.39936 | 0.91939 | 0.028814 |  | 0.057475
0.77269 | 1.0739e-06 | 0.46661 | 17209.9312 | 0.6212 | 0.88784 | 0.018757 |  | 0.28135 | 3.8363e-08 | 0.63909 | 47155.4716 | 0.29773 | 0.8912 | 0.0011717 | 0.97537 | 2.8665e-06 | 0.88076 | 55589.9841 | 0.97897 | 0.98449 | 0.082335 |  | 0.10226
0.69679 | 9.2244e-07 | 0.4735 | 17269.6082 | 0.20287 | 0.82101 | 0.021003 |  | 0.31424 | 4.2377e-08 | 0.63041 | 46938.2421 | 0.42614 | 0.90723 | 0.0012467 | 0.7668 | 1.7084e-06 | 0.056536 | 31987.2702 | 0.30273 | 0.90724 | 0.038671 |  | 0.06092
0.32611 | 4.4479e-07 | 0.29549 | 15717.2852 | 0.61966 | 0.88763 | 0.0074811 |  | 0.0011985 | 7.8288e-10 | 0.040001 | 30941.8513 | 0.28113 | 0.88882 | 1.839e-05 | 0.40016 | 1.0476e-06 | 0.023588 | 29526.876 | 0.56749 | 0.93695 | 0.020277 |  | 0.027777
0.354 | 4.742e-07 | 0.34388 | 16149.1572 | 0.19654 | 0.81952 | 0.010635 |  | 0.64514 | 9.2712e-08 | 0.13111 | 35093.5166 | 0.23885 | 0.88228 | 0.0023914 | 0.53742 | 1.2569e-06 | 0.065274 | 32455.0223 | 0.74225 | 0.95362 | 0.024557 |  | 0.037583
0.75785 | 1.0412e-06 | 0.99337 | 28719.2092 | 0.84809 | 0.92092 | 0.020982 |  | 0.74531 | 1.1597e-07 | 0.65706 | 47614.3124 | 0.93672 | 0.96493 | 0.0030203 | 0.81544 | 1.845e-06 | 0.34036 | 40445.1797 | 0.83105 | 0.96259 | 0.04196 |  | 0.065962
0.32996 | 4.4883e-07 | 0.025206 | 11833.7459 | 0.99705 | 0.97242 | 0.0036669 |  | 0.33383 | 4.4811e-08 | 0.066129 | 32498.48 | 0.90626 | 0.95976 | 0.00085682 | 0.059869 | 4.7387e-07 | 0.4591 | 43021.6022 | 0.73679 | 0.95309 | 0.011662 |  | 0.016186
0.28927 | 4.0643e-07 | 0.025701 | 11853.4923 | 0.19946 | 0.82021 | 0.0083768 |  | 0.81828 | 1.3893e-07 | 0.42583 | 42302.4067 | 0.13811 | 0.86211 | 0.0042115 | 0.20596 | 7.5864e-07 | 0.59977 | 46191.3843 | 0.75068 | 0.95444 | 0.019751 |  | 0.032339
0.88557 | 1.4153e-06 | 0.01774 | 11492.3214 | 0.7437 | 0.90465 | 0.019179 |  | 0.72432 | 1.1049e-07 | 0.051242 | 31679.1817 | 0.28335 | 0.88914 | 0.0026291 | 0.74814 | 1.662e-06 | 0.39073 | 41544.4376 | 0.15594 | 0.88151 | 0.047683 |  | 0.069492
0.88247 | 1.4024e-06 | 0.36673 | 16348.5265 | 0.13199 | 0.80168 | 0.033554 |  | 0.55904 | 7.6933e-08 | 0.27146 | 38883.2923 | 0.28496 | 0.88938 | 0.0020758 | 0.13744 | 6.4242e-07 | 0.52954 | 44570.2705 | 0.91625 | 0.97284 | 0.015456 |  | 0.051086
0.5588 | 7.1306e-07 | 0.63919 | 18793.3165 | 0.18788 | 0.81741 | 0.016882 |  | 0.32864 | 4.4163e-08 | 0.66856 | 47915.1258 | 0.48528 | 0.91371 | 0.0013006 | 0.26354 | 8.4732e-07 | 0.16221 | 36059.3143 | 0.15416 | 0.88109 | 0.022286 |  | 0.040469
0.69508 | 9.1943e-07 | 0.6678 | 19087.1305 | 0.77952 | 0.9099 | 0.015241 |  | 0.51738 | 7.0197e-08 | 0.078224 | 33076.436 | 0.61038 | 0.92654 | 0.0015274 | 0.46105 | 1.138e-06 | 0.27673 | 39006.4892 | 0.76211 | 0.95556 | 0.02564 |  | 0.042408
0.27667 | 3.9337e-07 | 0.53895 | 17846.3909 | 0.3016 | 0.84097 | 0.0084322 |  | 0.83117 | 1.4386e-07 | 0.8307 | 53177.2127 | 0.76743 | 0.94256 | 0.0043292 | 0.48269 | 1.171e-06 | 0.029117 | 30067.8654 | 0.97385 | 0.98312 | 0.019038 |  | 0.0318
0.36283 | 4.8359e-07 | 0.45562 | 17114.9212 | 0.43831 | 0.86272 | 0.0093856 |  | 0.51115 | 6.9229e-08 | 0.59968 | 46189.3572 | 0.43268 | 0.90797 | 0.0020098 | 0.39302 | 1.0372e-06 | 0.56574 | 45392.6468 | 0.44681 | 0.92468 | 0.028611 |  | 0.040006
0.34823 | 4.6809e-07 | 0.5261 | 17731.4666 | 0.20129 | 0.82064 | 0.01076 |  | 0.013946 | 4.1147e-09 | 0.56577 | 45393.4812 | 0.61425 | 0.92692 | 0.00011291 | 0.57112 | 1.3123e-06 | 0.03248 | 30360.3947 | 0.44808 | 0.92481 | 0.027067 |  | 0.03794
0.97376 | 2.0983e-06 | 0.13502 | 14036.3381 | 0.045461 | 0.76008 | 0.055292 |  | 0.84827 | 1.5098e-07 | 0.75535 | 50427.0089 | 0.036235 | 0.81994 | 0.0055028 | 0.66802 | 1.4879e-06 | 0.26344 | 38694.1016 | 0.84579 | 0.9642 | 0.032422 |  | 0.093216
0.82461 | 1.2056e-06 | 0.0084118 | 10849.6889 | 0.85891 | 0.92284 | 0.014184 |  | 0.99768 | 4.131e-07 | 0.77333 | 51019.965 | 0.94915 | 0.96742 | 0.011374 | 0.064122 | 4.8526e-07 | 0.79723 | 51862.7478 | 0.77226 | 0.95656 | 0.013883 |  | 0.039441
0.68485 | 9.0162e-07 | 0.51923 | 17670.3255 | 0.96299 | 0.94815 | 0.011648 |  | 0.073027 | 1.3209e-08 | 0.38968 | 41521.5418 | 0.46326 | 0.91134 | 0.00035251 | 0.66605 | 1.484e-06 | 0.80228 | 52050.0147 | 0.76444 | 0.95579 | 0.042661 |  | 0.054661
0.79266 | 1.1211e-06 | 0.18317 | 14608.1204 | 0.53903 | 0.8768 | 0.019279 |  | 0.48143 | 6.4742e-08 | 0.47161 | 43293.4981 | 0.90737 | 0.95993 | 0.0015725 | 0.87879 | 2.0772e-06 | 0.81605 | 52579.4766 | 0.79013 | 0.95834 | 0.059914 |  | 0.080765
0.42953 | 5.5649e-07 | 0.44346 | 17010.0343 | 0.4482 | 0.86415 | 0.010712 |  | 0.52901 | 7.2029e-08 | 0.36039 | 40884.8965 | 0.40802 | 0.90516 | 0.0019312 | 0.67718 | 1.5061e-06 | 0.07993 | 33153.1197 | 0.78855 | 0.95819 | 0.029439 |  | 0.042083
0.7388 | 1.0016e-06 | 0.54172 | 17871.3462 | 0.23186 | 0.82746 | 0.022545 |  | 0.44124 | 5.897e-08 | 0.362 | 40920.0248 | 0.0056235 | 0.77024 | 0.0021162 | 0.79666 | 1.7892e-06 | 0.76593 | 50771.9277 | 0.65715 | 0.94552 | 0.051484 |  | 0.076146
0.21605 | 3.3052e-07 | 0.035524 | 12197.2659 | 0.096805 | 0.7888 | 0.007705 |  | 0.62816 | 8.9359e-08 | 0.81292 | 52456.7179 | 0.32239 | 0.89457 | 0.0029219 | 0.91846 | 2.2845e-06 | 0.80474 | 52142.3222 | 0.74804 | 0.95418 | 0.066001 |  | 0.076628
0.7449 | 1.014e-06 | 0.37421 | 16413.4256 | 0.82164 | 0.91647 | 0.015047 |  | 0.10339 | 1.7101e-08 | 0.25698 | 38540.4216 | 0.36531 | 0.90006 | 0.00044632 | 0.84531 | 1.9443e-06 | 0.016547 | 28675.8944 | 0.77907 | 0.95724 | 0.033969 |  | 0.049462
0.29941 | 4.1695e-07 | 0.96865 | 25393.7743 | 0.46626 | 0.86673 | 0.009456 |  | 0.69817 | 1.0417e-07 | 0.3735 | 41170.7136 | 0.17481 | 0.87049 | 0.0030483 | 0.19076 | 7.3417e-07 | 0.96203 | 62626.6805 | 0.25429 | 0.9001 | 0.027118 |  | 0.039622
0.67258 | 8.8088e-07 | 0.67891 | 19205.135 | 0.81573 | 0.91551 | 0.014263 |  | 0.43763 | 5.8466e-08 | 0.35128 | 40685.4384 | 0.69708 | 0.93524 | 0.001444 | 0.43657 | 1.1014e-06 | 0.42632 | 42312.9122 | 0.97889 | 0.98446 | 0.024438 |  | 0.040146
0.094283 | 1.9534e-07 | 0.9491 | 24275.8497 | 0.053891 | 0.76627 | 0.0058165 |  | 0.025024 | 6.1626e-09 | 0.22784 | 37827.8584 | 0.63068 | 0.92857 | 0.0001468 | 0.56 | 1.2938e-06 | 0.65239 | 47493.9912 | 0.79236 | 0.95857 | 0.034146 |  | 0.040109
0.29436 | 4.1171e-07 | 0.7664 | 20239.8801 | 0.8407 | 0.91965 | 0.0067296 |  | 0.079847 | 1.4105e-08 | 0.71074 | 49075.3349 | 0.53154 | 0.91855 | 0.00041856 | 0.027099 | 3.6467e-07 | 0.23906 | 38106.3478 | 0.094183 | 0.86393 | 0.01035 |  | 0.017498
0.51167 | 6.5292e-07 | 0.36306 | 16316.6487 | 0.67115 | 0.89456 | 0.010796 |  | 0.69137 | 1.026e-07 | 0.37242 | 41147.1174 | 0.44535 | 0.90938 | 0.0027341 | 0.29692 | 8.9688e-07 | 0.43412 | 42481.3832 | 0.60171 | 0.94025 | 0.022606 |  | 0.036136
0.96754 | 2.0023e-06 | 0.56559 | 18088.4854 | 0.2364 | 0.82842 | 0.045098 |  | 0.32836 | 4.4128e-08 | 0.99627 | 74991.9831 | 0.30131 | 0.8917 | 0.0018941 | 0.90704 | 2.217e-06 | 0.062553 | 32314.1845 | 0.95971 | 0.97997 | 0.038993 |  | 0.085985
0.21641 | 3.3089e-07 | 0.80992 | 20858.5112 | 0.8628 | 0.92355 | 0.0054032 |  | 0.84435 | 1.4928e-07 | 0.12612 | 34926.862 | 0.1527 | 0.86564 | 0.0040138 | 0.47398 | 1.1577e-06 | 0.72156 | 49389.7827 | 0.83673 | 0.96321 | 0.031268 |  | 0.040685
0.4766 | 6.1064e-07 | 0.49402 | 17448.3418 | 0.25355 | 0.83193 | 0.013423 |  | 0.42446 | 5.6648e-08 | 0.8301 | 53152.2463 | 0.21117 | 0.87752 | 0.0019289 | 0.11304 | 5.9579e-07 | 0.50105 | 43937.5527 | 0.89021 | 0.9694 | 0.014286 |  | 0.029637
0.32497 | 4.436e-07 | 0.82184 | 21046.2842 | 0.51196 | 0.8731 | 0.0090069 |  | 0.41435 | 5.527e-08 | 0.82135 | 52791.38 | 0.27164 | 0.88741 | 0.0018398 | 0.33189 | 9.4806e-07 | 0.87656 | 55359.0094 | 0.6382 | 0.94372 | 0.029439 |  | 0.040285
0.2138 | 3.2817e-07 | 0.529 | 17757.2827 | 0.91677 | 0.93464 | 0.0046023 |  | 0.75794 | 1.1946e-07 | 0.89297 | 56302.7056 | 0.68789 | 0.93431 | 0.0038296 | 0.013352 | 2.9284e-07 | 0.90505 | 57078.2604 | 0.43036 | 0.92288 | 0.0096911 |  | 0.018123
0.90263 | 1.4928e-06 | 0.22148 | 15011.2885 | 0.96033 | 0.94715 | 0.017523 |  | 0.19689 | 2.832e-08 | 0.77713 | 51149.3208 | 0.93123 | 0.96391 | 0.00078767 | 0.62409 | 1.4047e-06 | 0.46035 | 43048.7856 | 0.27224 | 0.90285 | 0.039253 |  | 0.057564
0.23787 | 3.5322e-07 | 0.72192 | 19686.952 | 0.63957 | 0.8903 | 0.0064899 |  | 0.10241 | 1.6979e-08 | 0.85236 | 54139.6248 | 0.2964 | 0.89101 | 0.00057164 | 0.45153 | 1.1237e-06 | 0.7671 | 50810.7353 | 0.34415 | 0.91273 | 0.034648 |  | 0.04171
0.69632 | 9.2161e-07 | 0.27292 | 15509.373 | 0.49219 | 0.87037 | 0.016686 |  | 0.040187 | 8.5944e-09 | 0.3003 | 39548.9315 | 0.99309 | 0.98236 | 0.00018023 | 0.087112 | 5.41e-07 | 0.071069 | 32742.3537 | 0.18423 | 0.88764 | 0.013187 |  | 0.030053
0.48434 | 6.1981e-07 | 0.47749 | 17304.316 | 0.26631 | 0.83443 | 0.013465 |  | 0.39836 | 5.3126e-08 | 0.50335 | 43988.409 | 0.75475 | 0.94121 | 0.0013734 | 0.11035 | 5.904e-07 | 0.38722 | 41468.4347 | 0.25244 | 0.8998 | 0.016197 |  | 0.031035
0.097584 | 1.9941e-07 | 0.62362 | 18638.8177 | 0.33516 | 0.84675 | 0.0042507 |  | 0.89845 | 1.7741e-07 | 0.80459 | 52136.8694 | 0.87607 | 0.95541 | 0.0051114 | 0.9415 | 2.4516e-06 | 0.46556 | 43161.9308 | 0.094512 | 0.86404 | 0.074912 |  | 0.084274
0.56147 | 7.1661e-07 | 0.23345 | 15130.8964 | 0.78597 | 0.91087 | 0.010533 |  | 0.057647 | 1.1123e-08 | 0.71676 | 49249.1681 | 0.64652 | 0.93015 | 0.00032282 | 0.68102 | 1.5139e-06 | 0.20113 | 37141.0999 | 0.32762 | 0.9106 | 0.037456 |  | 0.048312
0.29578 | 4.1318e-07 | 0.29067 | 15673.3208 | 0.44401 | 0.86355 | 0.0077349 |  | 0.22645 | 3.1809e-08 | 0.82546 | 52959.1536 | 0.98525 | 0.97794 | 0.00088518 | 0.1116 | 5.9293e-07 | 0.67784 | 48162.2566 | 0.35094 | 0.91358 | 0.017533 |  | 0.026153
0.9898 | 2.5175e-06 | 0.90541 | 22756.3916 | 0.91566 | 0.93438 | 0.041238 |  | 0.92 | 1.9288e-07 | 0.66048 | 47703.3429 | 0.28067 | 0.88875 | 0.0059684 | 0.26327 | 8.4691e-07 | 0.49581 | 43822.2777 | 0.96655 | 0.98141 | 0.019591 |  | 0.066798
0.76399 | 1.0545e-06 | 0.052301 | 12649.9914 | 0.042243 | 0.75746 | 0.027457 |  | 0.95578 | 2.3084e-07 | 0.57643 | 45640.7436 | 0.77816 | 0.94372 | 0.0061093 | 0.33341 | 9.5028e-07 | 0.85866 | 54440.6195 | 0.091033 | 0.86279 | 0.03374 |  | 0.067307
0.84791 | 1.2764e-06 | 0.037419 | 12255.2521 | 0.82032 | 0.91626 | 0.01653 |  | 0.58606 | 8.1581e-08 | 0.59523 | 46083.1871 | 0.17151 | 0.8698 | 0.0025655 | 0.14199 | 6.5071e-07 | 0.46681 | 43189.0924 | 0.45334 | 0.92538 | 0.017257 |  | 0.036353
0.71796 | 9.6111e-07 | 0.93199 | 23579.8692 | 0.24442 | 0.83008 | 0.023712 |  | 0.15806 | 2.3727e-08 | 0.51069 | 44150.4043 | 0.3765 | 0.90143 | 0.00067703 | 0.35671 | 9.8421e-07 | 0.93075 | 59058.0347 | 0.97947 | 0.98463 | 0.029941 |  | 0.054331
0.16984 | 2.8161e-07 | 0.52287 | 17702.6709 | 0.79584 | 0.91238 | 0.0044356 |  | 0.43578 | 5.821e-08 | 0.9596 | 62269.0014 | 0.39342 | 0.90345 | 0.0021297 | 0.67197 | 1.4957e-06 | 0.66565 | 47838.5874 | 0.64354 | 0.94423 | 0.041088 |  | 0.047653
0.84762 | 1.2755e-06 | 0.35938 | 16284.6158 | 0.71351 | 0.90038 | 0.020482 |  | 0.42184 | 5.6289e-08 | 0.99619 | 74886.7666 | 0.39626 | 0.90379 | 0.0023793 | 0.94127 | 2.4497e-06 | 0.87845 | 55462.1557 | 0.27451 | 0.90319 | 0.082131 |  | 0.10499
0.68966 | 9.0994e-07 | 0.80754 | 20822.1055 | 0.45553 | 0.86521 | 0.018941 |  | 0.067832 | 1.2516e-08 | 0.28345 | 39162.5765 | 0.96092 | 0.97011 | 0.00027052 | 0.85601 | 1.9839e-06 | 0.3298 | 40211.5406 | 0.27608 | 0.90343 | 0.052818 |  | 0.07203
0.74904 | 1.0226e-06 | 0.95651 | 24644.6153 | 0.4377 | 0.86264 | 0.023175 |  | 0.31351 | 4.2287e-08 | 0.67969 | 48212.024 | 0.31376 | 0.89341 | 0.0013056 | 0.16198 | 6.86e-07 | 0.023161 | 29481.2436 | 0.7585 | 0.9552 | 0.012351 |  | 0.036832
0.10829 | 2.1234e-07 | 0.43673 | 16952.1297 | 0.41067 | 0.85865 | 0.0041747 |  | 0.8115 | 1.3646e-07 | 0.15361 | 35802.9154 | 0.43418 | 0.90814 | 0.0033166 | 0.81957 | 1.8579e-06 | 0.708 | 48996.8084 | 0.40704 | 0.92027 | 0.054863 |  | 0.062355
0.99477 | 2.8082e-06 | 0.14232 | 14129.2872 | 0.17051 | 0.81296 | 0.062141 |  | 0.50629 | 6.8482e-08 | 0.96975 | 63923.4016 | 0.6011 | 0.9256 | 0.0024723 | 0.13494 | 6.378e-07 | 0.67398 | 48059.1449 | 0.41951 | 0.92168 | 0.018502 |  | 0.083115
0.36732 | 4.884e-07 | 0.94949 | 24294.0374 | 0.96964 | 0.95085 | 0.0077437 |  | 0.13073 | 2.0454e-08 | 0.43244 | 42445.0428 | 0.24544 | 0.88335 | 0.00059246 | 0.75536 | 1.6796e-06 | 0.22703 | 37807.6335 | 0.48847 | 0.92907 | 0.039935 |  | 0.048271
0.7408 | 1.0057e-06 | 0.84261 | 21397.9907 | 0.3658 | 0.85174 | 0.022226 |  | 0.28128 | 3.8355e-08 | 0.62526 | 46810.6682 | 0.98148 | 0.97636 | 0.00095592 | 0.76891 | 1.7138e-06 | 0.28145 | 39116.2968 | 0.049974 | 0.84343 | 0.051778 |  | 0.07496
0.71956 | 9.6413e-07 | 0.46523 | 17197.9815 | 0.064972 | 0.77324 | 0.025563 |  | 0.17295 | 2.5493e-08 | 0.02138 | 29283.8626 | 0.30599 | 0.89235 | 0.0005735 | 0.59937 | 1.3607e-06 | 0.77188 | 50971.0684 | 0.29349 | 0.90595 | 0.042627 |  | 0.068763
0.045916 | 1.2889e-07 | 0.52944 | 17761.1792 | 0.74865 | 0.90536 | 0.0021048 |  | 0.0030661 | 1.4715e-09 | 0.40919 | 41943.3771 | 0.16592 | 0.8686 | 4.3742e-05 | 0.38449 | 1.0247e-06 | 0.31194 | 39812.1369 | 0.18742 | 0.88828 | 0.028147 |  | 0.030296
0.54531 | 6.9541e-07 | 0.96017 | 24848.2399 | 0.8661 | 0.92415 | 0.012605 |  | 0.33248 | 4.4642e-08 | 0.86782 | 54898.0624 | 0.14136 | 0.86292 | 0.0015935 | 0.31874 | 9.2887e-07 | 0.86542 | 54775.368 | 0.78691 | 0.95802 | 0.027788 |  | 0.041986
0.98778 | 2.438e-06 | 0.93699 | 23765.5971 | 0.16164 | 0.81055 | 0.063942 |  | 0.85341 | 1.5327e-07 | 0.65251 | 47496.8988 | 0.69543 | 0.93507 | 0.0042753 | 0.44275 | 1.1106e-06 | 0.77504 | 51077.9387 | 0.69321 | 0.94893 | 0.031883 |  | 0.1001
0.21089 | 3.2512e-07 | 0.15 | 14224.45 | 0.96232 | 0.94789 | 0.0036759 |  | 0.36896 | 4.9274e-08 | 0.44491 | 42714.4965 | 0.57192 | 0.92267 | 0.0013048 | 0.56894 | 1.3087e-06 | 0.49953 | 43904.2174 | 0.25819 | 0.90071 | 0.037258 |  | 0.042239
0.63782 | 8.2536e-07 | 0.67932 | 19209.51 | 0.51978 | 0.87417 | 0.016027 |  | 0.61086 | 8.6077e-08 | 0.25309 | 38447.2399 | 0.36863 | 0.90047 | 0.0022405 | 0.37794 | 1.0151e-06 | 0.6259 | 46826.4688 | 0.40646 | 0.9202 | 0.028967 |  | 0.047235
0.98698 | 2.4099e-06 | 0.4992 | 17493.7598 | 0.96702 | 0.94974 | 0.03063 |  | 0.29805 | 4.0391e-08 | 0.7484 | 50206.2598 | 0.20382 | 0.87618 | 0.0013265 | 0.087682 | 5.4228e-07 | 0.86817 | 54915.6625 | 0.741 | 0.9535 | 0.016406 |  | 0.048363
0.12315 | 2.2975e-07 | 0.75194 | 20052.8084 | 0.92615 | 0.93693 | 0.0034276 |  | 0.062434 | 1.1783e-08 | 0.8641 | 54709.1636 | 0.62196 | 0.92769 | 0.00037366 | 0.6108 | 1.3808e-06 | 0.23951 | 38117.2611 | 0.41685 | 0.92138 | 0.033758 |  | 0.03756
0.3237 | 4.4227e-07 | 0.65108 | 18913.7874 | 0.17397 | 0.81387 | 0.010615 |  | 0.42484 | 5.67e-08 | 0.52051 | 44368.6636 | 0.41045 | 0.90544 | 0.0016086 | 0.66274 | 1.4775e-06 | 0.057976 | 32067.5757 | 0.61806 | 0.94181 | 0.029843 |  | 0.042066
0.34203 | 4.6153e-07 | 0.36648 | 16346.3891 | 0.2959 | 0.83994 | 0.0096395 |  | 0.47856 | 6.4319e-08 | 0.93739 | 59673.6143 | 0.21564 | 0.87832 | 0.0023712 | 0.50444 | 1.2046e-06 | 0.23105 | 37908.028 | 0.17602 | 0.88594 | 0.032263 |  | 0.044274
0.07945 | 1.7651e-07 | 0.067847 | 12985.5924 | 0.2891 | 0.83871 | 0.0034551 |  | 0.27092 | 3.7107e-08 | 0.2173 | 37561.3662 | 0.85576 | 0.95275 | 0.00081754 | 0.86034 | 2.0006e-06 | 0.89208 | 56248.397 | 0.050372 | 0.84367 | 0.074865 |  | 0.079138
0.84695 | 1.2733e-06 | 0.76179 | 20179.275 | 0.19353 | 0.81879 | 0.030732 |  | 0.71642 | 1.0852e-07 | 0.17054 | 36300.6669 | 0.24005 | 0.88248 | 0.0028555 | 0.94059 | 2.444e-06 | 0.48104 | 43498.9294 | 0.55694 | 0.93593 | 0.063468 |  | 0.097055
0.25799 | 3.7405e-07 | 0.14424 | 14153.3024 | 0.034124 | 0.74997 | 0.010178 |  | 0.12742 | 2.0053e-08 | 0.17616 | 36460.4203 | 0.33343 | 0.89602 | 0.0005102 | 0.70634 | 1.5668e-06 | 0.34652 | 40580.9617 | 0.67734 | 0.94742 | 0.037336 |  | 0.048024
0.37667 | 4.9843e-07 | 0.31152 | 15862.1791 | 0.51064 | 0.87292 | 0.0089992 |  | 0.91625 | 1.8993e-07 | 0.26261 | 38674.5877 | 0.86881 | 0.95444 | 0.0042633 | 0.19283 | 7.3754e-07 | 0.32347 | 40070.438 | 0.38073 | 0.91721 | 0.018902 |  | 0.032165
0.19156 | 3.0479e-07 | 0.16353 | 14385.7507 | 0.68233 | 0.89608 | 0.004739 |  | 0.42686 | 5.6976e-08 | 0.60603 | 46341.7484 | 0.60061 | 0.92556 | 0.0015935 | 0.90125 | 2.1856e-06 | 0.40367 | 41824.1172 | 0.046833 | 0.84141 | 0.06882 |  | 0.075152
0.64939 | 8.4335e-07 | 0.61529 | 18557.4583 | 0.42279 | 0.86045 | 0.017043 |  | 0.43484 | 5.8079e-08 | 0.56157 | 45296.691 | 0.12139 | 0.85767 | 0.0018523 | 0.58616 | 1.3378e-06 | 0.0099592 | 27568.3522 | 0.19193 | 0.88918 | 0.029385 |  | 0.04828
0.13616 | 2.4457e-07 | 0.29629 | 15724.5806 | 0.49417 | 0.87065 | 0.0044454 |  | 0.4614 | 6.1826e-08 | 0.47522 | 43372.0376 | 0.4525 | 0.91017 | 0.0017068 | 0.10755 | 5.8472e-07 | 0.15694 | 35902.8913 | 0.3485 | 0.91328 | 0.014028 |  | 0.020181
0.90256 | 1.4925e-06 | 0.30254 | 15781.2245 | 0.51675 | 0.87376 | 0.026795 |  | 0.9377 | 2.0897e-07 | 0.40324 | 41814.7298 | 0.50184 | 0.91546 | 0.0055473 | 0.38756 | 1.0292e-06 | 0.62081 | 46700.982 | 0.2419 | 0.89811 | 0.03077 |  | 0.063112
0.68893 | 9.0866e-07 | 0.51976 | 17675.0286 | 0.39483 | 0.85626 | 0.018318 |  | 0.59195 | 8.2628e-08 | 0.64958 | 47421.9239 | 0.14993 | 0.86499 | 0.0026719 | 0.82984 | 1.8911e-06 | 0.82043 | 52754.161 | 0.11619 | 0.87109 | 0.064805 |  | 0.085795
0.87465 | 1.3712e-06 | 0.1139 | 13749.9453 | 0.81427 | 0.91528 | 0.018804 |  | 0.57048 | 7.8872e-08 | 0.24618 | 38280.2818 | 0.42765 | 0.9074 | 0.0020096 | 0.34521 | 9.6746e-07 | 0.26279 | 38678.8618 | 0.089912 | 0.86237 | 0.027799 |  | 0.048613
0.28172 | 3.986e-07 | 0.65319 | 18935.4253 | 0.27669 | 0.83641 | 0.0088687 |  | 0.5563 | 7.6473e-08 | 0.28407 | 39176.9362 | 0.89187 | 0.95762 | 0.0017184 | 0.15807 | 6.7924e-07 | 0.13612 | 35256.8493 | 0.42159 | 0.92191 | 0.015685 |  | 0.026272
0.92943 | 1.6451e-06 | 0.055928 | 12733.8375 | 0.59946 | 0.88492 | 0.025852 |  | 0.52184 | 7.0895e-08 | 0.56672 | 45415.3282 | 0.7025 | 0.93579 | 0.0019052 | 0.70563 | 1.5652e-06 | 0.47543 | 43376.5808 | 0.31201 | 0.90852 | 0.043386 |  | 0.071143
0.46499 | 5.9703e-07 | 0.42371 | 16840.0557 | 0.78045 | 0.91004 | 0.0092798 |  | 0.43123 | 5.7579e-08 | 0.9017 | 56854.864 | 0.014363 | 0.7943 | 0.0023377 | 0.75355 | 1.6751e-06 | 0.72285 | 49427.8223 | 0.94239 | 0.97682 | 0.043841 |  | 0.055459
0.88612 | 1.4177e-06 | 0.43676 | 16952.3359 | 0.52725 | 0.87519 | 0.026016 |  | 0.21705 | 3.0699e-08 | 0.40494 | 41851.5799 | 0.91768 | 0.96158 | 0.00072104 | 0.73638 | 1.6341e-06 | 0.14259 | 35463.1293 | 0.93359 | 0.9754 | 0.031783 |  | 0.05852
0.72576 | 9.7598e-07 | 0.85733 | 21669.8976 | 0.34889 | 0.84902 | 0.021887 |  | 0.61694 | 8.7217e-08 | 0.99361 | 72255.8373 | 0.44862 | 0.90974 | 0.0035562 | 0.41606 | 1.071e-06 | 0.80143 | 52018.0138 | 0.48683 | 0.9289 | 0.032546 |  | 0.057989
0.0055284 | 4.1486e-08 | 0.10363 | 13599.27 | 0.78294 | 0.91041 | 0.00058239 |  | 0.28958 | 3.936e-08 | 0.9902 | 70034.932 | 0.48587 | 0.91377 | 0.0015568 | 0.50418 | 1.2042e-06 | 0.16055 | 36010.2087 | 0.1436 | 0.87854 | 0.03186 |  | 0.034
0.13165 | 2.3947e-07 | 0.984 | 26872.9754 | 0.55385 | 0.8788 | 0.0053701 |  | 0.65844 | 9.5434e-08 | 0.44983 | 42820.8077 | 0.88992 | 0.95734 | 0.0023128 | 0.25756 | 8.3834e-07 | 0.23866 | 38096.3759 | 0.33521 | 0.91158 | 0.02105 |  | 0.028733
0.78981 | 1.1141e-06 | 0.10773 | 13660.4224 | 0.9376 | 0.93996 | 0.013012 |  | 0.11364 | 1.8371e-08 | 0.76254 | 50660.3389 | 0.55422 | 0.92087 | 0.00055585 | 0.20245 | 7.5304e-07 | 0.077377 | 33037.9697 | 0.95573 | 0.97919 | 0.013553 |  | 0.027121
0.60383 | 7.7498e-07 | 0.3773 | 16440.1641 | 0.37827 | 0.8537 | 0.015371 |  | 0.55889 | 7.6907e-08 | 0.71711 | 49259.3016 | 0.63303 | 0.9288 | 0.002239 | 0.91602 | 2.2694e-06 | 0.54487 | 44915.6413 | 0.29291 | 0.90587 | 0.064882 |  | 0.082492
0.077621 | 1.7411e-07 | 0.33946 | 16110.2491 | 0.31636 | 0.84355 | 0.0035692 |  | 0.52069 | 7.0715e-08 | 0.77574 | 51101.7334 | 0.2788 | 0.88848 | 0.0022962 | 0.042307 | 4.2141e-07 | 0.64303 | 47255.0235 | 0.28177 | 0.90426 | 0.012538 |  | 0.018403
0.83536 | 1.2371e-06 | 0.37858 | 16451.2365 | 0.84194 | 0.91986 | 0.018046 |  | 0.067942 | 1.2531e-08 | 0.68282 | 48296.8669 | 0.05834 | 0.83411 | 0.00043449 | 0.92165 | 2.3049e-06 | 0.66235 | 47751.9887 | 0.55113 | 0.93536 | 0.064525 |  | 0.083006
0.21743 | 3.3196e-07 | 0.15028 | 14227.7651 | 0.47957 | 0.86861 | 0.005872 |  | 0.28811 | 3.9182e-08 | 0.30815 | 39726.6483 | 0.54853 | 0.92029 | 0.00098984 | 0.90569 | 2.2095e-06 | 0.25821 | 38569.7708 | 0.64468 | 0.94434 | 0.051012 |  | 0.057874
0.78294 | 1.0976e-06 | 0.8378 | 21313.4585 | 0.75601 | 0.90642 | 0.0196 |  | 0.024883 | 6.1384e-09 | 0.45827 | 43003.7286 | 0.98571 | 0.97815 | 0.00014085 | 0.16719 | 6.9493e-07 | 0.80993 | 52340.4124 | 0.77355 | 0.95669 | 0.020035 |  | 0.039777
0.50576 | 6.4566e-07 | 0.013531 | 11247.1958 | 0.28923 | 0.83873 | 0.012167 |  | 0.97492 | 2.6659e-07 | 0.75751 | 50496.5736 | 0.96315 | 0.97067 | 0.0072184 | 0.7991 | 1.7962e-06 | 0.71222 | 49117.9197 | 0.19595 | 0.88996 | 0.056572 |  | 0.075957
0.028335 | 9.8669e-08 | 0.92496 | 23338.4115 | 0.74957 | 0.90549 | 0.0018595 |  | 0.26467 | 3.6357e-08 | 0.086221 | 33427.0284 | 0.80404 | 0.94659 | 0.0007453 | 0.76222 | 1.6967e-06 | 0.5107 | 44150.7667 | 0.31651 | 0.90912 | 0.04756 |  | 0.050165
0.53055 | 6.7652e-07 | 0.59348 | 18348.4217 | 0.61306 | 0.88674 | 0.012215 |  | 0.48033 | 6.458e-08 | 0.57318 | 45565.063 | 0.015972 | 0.79713 | 0.0023205 | 0.68867 | 1.5295e-06 | 0.67236 | 48015.8581 | 0.84093 | 0.96366 | 0.040255 |  | 0.054791
0.24076 | 3.5621e-07 | 0.12251 | 13870.1242 | 0.93029 | 0.93799 | 0.0042521 |  | 0.23556 | 3.2888e-08 | 0.29056 | 39326.3233 | 0.13648 | 0.8617 | 0.0009557 | 0.42242 | 1.0804e-06 | 0.24455 | 38240.5925 | 0.86599 | 0.96648 | 0.023137 |  | 0.028345
0.22993 | 3.4497e-07 | 0.29339 | 15698.1983 | 0.42204 | 0.86034 | 0.0065501 |  | 0.48004 | 6.4536e-08 | 0.10313 | 34105.7388 | 0.19449 | 0.87442 | 0.0016723 | 0.60207 | 1.3654e-06 | 0.86946 | 54982.1585 | 0.13247 | 0.87567 | 0.047741 |  | 0.055964
0.88748 | 1.4235e-06 | 0.92115 | 23215.3376 | 0.025996 | 0.7407 | 0.044573 |  | 0.87066 | 1.6155e-07 | 0.25891 | 38586.4063 | 0.73349 | 0.93898 | 0.0037901 | 0.11498 | 5.9965e-07 | 0.53578 | 44710.3297 | 0.52769 | 0.93304 | 0.016025 |  | 0.064388
0.0061903 | 4.3995e-08 | 0.61129 | 18518.7499 | 0.8296 | 0.91778 | 0.00069075 |  | 0.41959 | 5.5982e-08 | 0.10547 | 34193.9818 | 0.62485 | 0.92798 | 0.0012414 | 0.091285 | 5.503e-07 | 0.95011 | 61033.5637 | 0.49749 | 0.92999 | 0.018992 |  | 0.020924
0.4245 | 5.5085e-07 | 0.092009 | 13417.3404 | 0.36575 | 0.85173 | 0.010302 |  | 0.7883 | 1.2861e-07 | 0.61091 | 46459.672 | 0.80559 | 0.94676 | 0.0034284 | 0.23024 | 7.967e-07 | 0.081773 | 33234.7592 | 0.19494 | 0.88976 | 0.019473 |  | 0.033204
0.10674 | 2.105e-07 | 0.99913 | 32727.4929 | 0.19952 | 0.82022 | 0.0061403 |  | 0.84766 | 1.5071e-07 | 0.0052679 | 26329.7428 | 0.21582 | 0.87835 | 0.0033488 | 0.069147 | 4.9822e-07 | 0.021492 | 29296.6039 | 0.97443 | 0.98327 | 0.0079062 |  | 0.017395
0.66551 | 8.6922e-07 | 0.40518 | 16680.6765 | 0.58748 | 0.88332 | 0.015288 |  | 0.46231 | 6.1957e-08 | 0.89643 | 56516.9665 | 0.18866 | 0.87329 | 0.0022167 | 0.012328 | 2.8587e-07 | 0.2122 | 37430.3529 | 0.34517 | 0.91286 | 0.0070661 |  | 0.024571
0.76081 | 1.0476e-06 | 0.84936 | 21520.0499 | 0.39775 | 0.8567 | 0.022807 |  | 0.91173 | 1.8652e-07 | 0.81097 | 52380.6967 | 0.8945 | 0.958 | 0.0053661 | 0.25513 | 8.3467e-07 | 0.74055 | 49961.4232 | 0.68702 | 0.94834 | 0.023551 |  | 0.051724
0.60902 | 7.8246e-07 | 0.54139 | 17868.3858 | 0.90841 | 0.93271 | 0.011132 |  | 0.1206 | 1.9223e-08 | 0.31597 | 39902.6396 | 0.44114 | 0.90891 | 0.00050197 | 0.44587 | 1.1152e-06 | 0.77669 | 51134.5435 | 0.16125 | 0.88272 | 0.036627 |  | 0.048261
0.99519 | 2.8443e-06 | 0.81486 | 20935.3268 | 0.79566 | 0.91236 | 0.049002 |  | 0.13691 | 2.12e-08 | 0.43182 | 42431.6284 | 0.87598 | 0.9554 | 0.00051253 | 0.49718 | 1.1933e-06 | 0.068108 | 32597.5981 | 0.2288 | 0.89592 | 0.028305 |  | 0.077819
0.1859 | 2.9878e-07 | 0.19264 | 14711.0817 | 0.54306 | 0.87734 | 0.0051385 |  | 0.75171 | 1.1772e-07 | 0.92234 | 58348.9277 | 0.42645 | 0.90727 | 0.0040722 | 0.35389 | 9.8011e-07 | 0.89544 | 56454.7817 | 0.79879 | 0.95922 | 0.030039 |  | 0.039249
0.81093 | 1.1678e-06 | 0.91445 | 23011.2756 | 0.54049 | 0.87699 | 0.024367 |  | 0.31353 | 4.229e-08 | 0.60768 | 46381.4208 | 0.0093901 | 0.78319 | 0.0015713 | 0.63091 | 1.4172e-06 | 0.03525 | 30584.9094 | 0.21367 | 0.89326 | 0.03261 |  | 0.058549
0.84009 | 1.2516e-06 | 0.8186 | 20994.2769 | 0.12832 | 0.80048 | 0.032393 |  | 0.26585 | 3.6498e-08 | 0.94655 | 60625.1435 | 0.68365 | 0.93388 | 0.0012446 | 0.39855 | 1.0453e-06 | 0.089182 | 33551.5622 | 0.52427 | 0.9327 | 0.022518 |  | 0.056156
0.18351 | 2.9624e-07 | 0.27421 | 15521.4009 | 0.289 | 0.83869 | 0.0061142 |  | 0.49696 | 6.7061e-08 | 0.81643 | 52594.6992 | 0.28889 | 0.88994 | 0.002216 | 0.87106 | 2.044e-06 | 0.14565 | 35558.7342 | 0.80531 | 0.95989 | 0.042064 |  | 0.050394
0.3743 | 4.9588e-07 | 0.37348 | 16407.1272 | 0.58799 | 0.88339 | 0.0086591 |  | 0.38998 | 5.2016e-08 | 0.78022 | 51255.7999 | 0.95103 | 0.96782 | 0.0014368 | 0.80945 | 1.8267e-06 | 0.76885 | 50869.1652 | 0.058325 | 0.84829 | 0.063689 |  | 0.073785
0.5696 | 7.2748e-07 | 0.77579 | 20365.7927 | 0.17089 | 0.81306 | 0.017936 |  | 0.97013 | 2.5561e-07 | 0.41012 | 41963.3622 | 0.82833 | 0.9494 | 0.0062248 | 0.56837 | 1.3077e-06 | 0.76838 | 50853.3891 | 0.17112 | 0.8849 | 0.042608 |  | 0.066769
0.30464 | 4.2239e-07 | 0.42852 | 16881.4573 | 0.47905 | 0.86854 | 0.0079608 |  | 0.62995 | 8.9706e-08 | 0.065226 | 32452.585 | 0.79103 | 0.94513 | 0.0018069 | 0.73293 | 1.6261e-06 | 0.49076 | 43711.599 | 0.86125 | 0.96594 | 0.03918 |  | 0.048948
0.33382 | 4.5289e-07 | 0.11766 | 13803.0949 | 0.97825 | 0.955 | 0.0047704 |  | 0.70685 | 1.0621e-07 | 0.18709 | 36763.6257 | 0.79524 | 0.9456 | 0.0023522 | 0.052236 | 4.5228e-07 | 0.43983 | 42604.6743 | 0.63279 | 0.94321 | 0.011337 |  | 0.01846
0.6493 | 8.4321e-07 | 0.79347 | 20613.4964 | 0.91431 | 0.93406 | 0.012988 |  | 0.32185 | 4.3319e-08 | 0.48199 | 43519.5731 | 0.60779 | 0.92627 | 0.0011529 | 0.83903 | 1.9222e-06 | 0.48886 | 43669.9058 | 0.025676 | 0.82329 | 0.064309 |  | 0.07845
0.26296 | 3.7919e-07 | 0.53533 | 17813.9548 | 0.49859 | 0.87126 | 0.0072191 |  | 0.90555 | 1.8212e-07 | 0.82023 | 52746.3901 | 0.52828 | 0.91821 | 0.0057151 | 0.21192 | 7.6809e-07 | 0.08188 | 33239.4439 | 0.59763 | 0.93986 | 0.016044 |  | 0.028978
0.21464 | 3.2905e-07 | 0.4884 | 17399.3177 | 0.12147 | 0.79815 | 0.0081029 |  | 0.43946 | 5.8721e-08 | 0.82821 | 53073.1681 | 0.82008 | 0.94843 | 0.0017432 | 0.76425 | 1.7019e-06 | 0.065729 | 32478.2 | 0.80035 | 0.95938 | 0.03257 |  | 0.042416
0.27188 | 3.8842e-07 | 0.71998 | 19664.1797 | 0.79302 | 0.91195 | 0.0064787 |  | 0.44714 | 5.9798e-08 | 0.72542 | 49503.6415 | 0.89861 | 0.9586 | 0.0016357 | 0.21782 | 7.7737e-07 | 0.56006 | 45261.9562 | 0.61396 | 0.94142 | 0.020551 |  | 0.028665
0.32304 | 4.4158e-07 | 0.28501 | 15621.3528 | 0.85449 | 0.92205 | 0.0061955 |  | 0.3672 | 4.9048e-08 | 0.52609 | 44493.0903 | 0.75589 | 0.94133 | 0.0012792 | 0.18423 | 7.2347e-07 | 0.58845 | 45922.627 | 0.56245 | 0.93646 | 0.019583 |  | 0.027058
0.52501 | 6.6953e-07 | 0.97105 | 25572.5877 | 0.31522 | 0.84336 | 0.016407 |  | 0.74291 | 1.1532e-07 | 0.3955 | 41647.5781 | 0.49136 | 0.91436 | 0.0030609 | 0.90821 | 2.2236e-06 | 0.30582 | 39674.1067 | 0.39491 | 0.91888 | 0.056333 |  | 0.075801
0.42906 | 5.5596e-07 | 0.56246 | 18059.7975 | 0.034829 | 0.75068 | 0.015911 |  | 0.77503 | 1.2447e-07 | 0.059046 | 32126.3883 | 0.12126 | 0.85764 | 0.0032671 | 0.63952 | 1.4332e-06 | 0.20398 | 37216.23 | 0.97979 | 0.98472 | 0.028179 |  | 0.047357
0.62402 | 8.0449e-07 | 0.57188 | 18146.4506 | 0.53618 | 0.87641 | 0.015107 |  | 0.72967 | 1.1185e-07 | 0.06128 | 32246.8671 | 0.50677 | 0.91598 | 0.0024751 | 0.59992 | 1.3617e-06 | 0.57493 | 45605.6144 | 0.31405 | 0.90879 | 0.039097 |  | 0.056679
0.51331 | 6.5495e-07 | 0.18744 | 14654.795 | 0.48744 | 0.86971 | 0.011649 |  | 0.92821 | 1.9987e-07 | 0.00028662 | 22053.0473 | 0.67291 | 0.9328 | 0.0032323 | 0.98293 | 3.0354e-06 | 0.14525 | 35546.4953 | 0.77071 | 0.95641 | 0.063188 |  | 0.07807
0.7649 | 1.0565e-06 | 0.24163 | 15211.1962 | 0.70506 | 0.89921 | 0.016554 |  | 0.11192 | 1.8158e-08 | 0.093721 | 33737.4103 | 0.048639 | 0.82861 | 0.00052642 | 0.13126 | 6.3097e-07 | 0.45386 | 42908.2428 | 0.88271 | 0.96847 | 0.014853 |  | 0.031933
0.1689 | 2.8058e-07 | 0.63236 | 18725.1623 | 0.58769 | 0.88335 | 0.0051877 |  | 0.70185 | 1.0502e-07 | 0.59368 | 46046.4146 | 0.72263 | 0.93785 | 0.0028395 | 0.24654 | 8.2167e-07 | 0.18198 | 36623.0084 | 0.52083 | 0.93236 | 0.018897 |  | 0.026924
0.61096 | 7.8527e-07 | 0.59184 | 18332.9641 | 0.011245 | 0.71381 | 0.024825 |  | 0.12183 | 1.9373e-08 | 0.014911 | 28438.7968 | 0.07648 | 0.84253 | 0.00049933 | 0.72619 | 1.6106e-06 | 0.76257 | 50661.4196 | 0.25576 | 0.90033 | 0.050795 |  | 0.076119
0.095756 | 1.9716e-07 | 0.07177 | 13061.8846 | 0.42416 | 0.86065 | 0.003515 |  | 0.57863 | 8.0278e-08 | 0.98733 | 68682.0661 | 0.41752 | 0.90625 | 0.0031577 | 0.43701 | 1.102e-06 | 0.15243 | 35767.1093 | 0.48893 | 0.92911 | 0.025154 |  | 0.031827
0.70247 | 9.326e-07 | 0.33521 | 16072.8568 | 0.63401 | 0.88955 | 0.01569 |  | 0.46889 | 6.2907e-08 | 0.92948 | 58946.7797 | 0.10775 | 0.85366 | 0.0023892 | 0.55135 | 1.2795e-06 | 0.70438 | 48893.7862 | 0.22991 | 0.89611 | 0.039676 |  | 0.057755
0.85263 | 1.292e-06 | 0.060074 | 12825.2323 | 0.31553 | 0.84341 | 0.02471 |  | 0.73045 | 1.1205e-07 | 0.88654 | 55919.6148 | 0.76219 | 0.942 | 0.0035204 | 0.18823 | 7.3004e-07 | 0.19053 | 36857.2499 | 0.86043 | 0.96584 | 0.015179 |  | 0.043409
0.4033 | 5.2737e-07 | 0.46382 | 17185.7608 | 0.49946 | 0.87138 | 0.0098908 |  | 0.19886 | 2.8552e-08 | 0.169 | 36256.4213 | 0.71568 | 0.93714 | 0.00064228 | 0.94208 | 2.4566e-06 | 0.9947 | 73213.0085 | 0.73899 | 0.95331 | 0.095777 |  | 0.10631
0.41518 | 5.4048e-07 | 0.81404 | 20922.3548 | 0.57405 | 0.88152 | 0.010594 |  | 0.42119 | 5.62e-08 | 0.37241 | 41146.853 | 0.049606 | 0.8292 | 0.0017996 | 0.62557 | 1.4074e-06 | 0.23966 | 38120.9843 | 0.49814 | 0.93006 | 0.033573 |  | 0.045966
0.23197 | 3.4709e-07 | 0.3219 | 15954.931 | 0.73689 | 0.90367 | 0.005431 |  | 0.63658 | 9.1004e-08 | 0.55508 | 45147.9677 | 0.018617 | 0.80127 | 0.0032303 | 0.31296 | 9.2042e-07 | 0.98174 | 66717.4126 | 0.60235 | 0.94031 | 0.033684 |  | 0.042345
0.2107 | 3.2493e-07 | 0.96088 | 24889.6982 | 0.074892 | 0.77867 | 0.0094486 |  | 0.79087 | 1.2944e-07 | 0.069048 | 32644.0119 | 0.29224 | 0.89042 | 0.0031238 | 0.42846 | 1.0893e-06 | 0.21485 | 37498.6512 | 0.81253 | 0.96064 | 0.023376 |  | 0.035949
0.9919 | 2.6182e-06 | 0.76293 | 20194.2541 | 0.12791 | 0.80034 | 0.066951 |  | 0.72416 | 1.1045e-07 | 0.61581 | 46578.7057 | 0.7386 | 0.93951 | 0.0030019 | 0.12813 | 6.2508e-07 | 0.21467 | 37494.1027 | 0.19188 | 0.88917 | 0.016488 |  | 0.086441
0.39612 | 5.1951e-07 | 0.37134 | 16388.5955 | 0.99995 | 0.98859 | 0.0047276 |  | 0.56079 | 7.7226e-08 | 0.82183 | 52810.8637 | 0.86759 | 0.95428 | 0.0022552 | 0.37343 | 1.0086e-06 | 0.79194 | 51670.0896 | 0.1206 | 0.87238 | 0.034006 |  | 0.040989
0.90448 | 1.502e-06 | 0.64636 | 18865.7528 | 0.12269 | 0.79857 | 0.037817 |  | 0.4197 | 5.5997e-08 | 0.89693 | 56548.0666 | 0.5562 | 0.92107 | 0.0018455 | 0.85809 | 1.9918e-06 | 0.58066 | 45739.3944 | 0.20338 | 0.89137 | 0.059558 |  | 0.099221
0.75702 | 1.0394e-06 | 0.41906 | 16800.0847 | 0.56556 | 0.88038 | 0.018579 |  | 0.76277 | 1.2085e-07 | 0.11947 | 34699.3592 | 0.3815 | 0.90203 | 0.0029283 | 0.23224 | 7.9979e-07 | 0.56987 | 45488.1944 | 0.92713 | 0.97441 | 0.019518 |  | 0.041025
0.19933 | 3.1299e-07 | 0.86273 | 21775.4236 | 0.879 | 0.9266 | 0.0051701 |  | 0.73209 | 1.1247e-07 | 0.26166 | 38652.0042 | 0.75004 | 0.94071 | 0.0026289 | 0.93994 | 2.4385e-06 | 0.02272 | 29433.5186 | 0.86082 | 0.96589 | 0.041951 |  | 0.04975
0.47825 | 6.1259e-07 | 0.1058 | 13631.7923 | 0.76763 | 0.90813 | 0.0087219 |  | 0.11335 | 1.8335e-08 | 0.58697 | 45887.673 | 0.49206 | 0.91443 | 0.00052212 | 0.28219 | 8.7513e-07 | 0.3113 | 39797.8418 | 0.91835 | 0.97313 | 0.019006 |  | 0.02825
0.35235 | 4.7244e-07 | 0.61953 | 18598.7414 | 0.63058 | 0.88909 | 0.0084962 |  | 0.63694 | 9.1076e-08 | 0.38585 | 41438.7045 | 0.66819 | 0.93232 | 0.0022993 | 0.39473 | 1.0397e-06 | 0.74857 | 50211.5856 | 0.70965 | 0.95049 | 0.029319 |  | 0.040114
0.20298 | 3.1683e-07 | 0.55564 | 17997.4132 | 0.46268 | 0.86622 | 0.0061825 |  | 0.22022 | 3.1073e-08 | 0.25967 | 38604.552 | 0.99335 | 0.98255 | 0.00063681 | 0.3668 | 9.9891e-07 | 0.34242 | 40490.745 | 0.92386 | 0.97393 | 0.021977 |  | 0.028797
0.36255 | 4.833e-07 | 0.72162 | 19683.4271 | 0.1658 | 0.81169 | 0.011833 |  | 0.88723 | 1.7055e-07 | 0.24018 | 38133.6629 | 0.74012 | 0.93967 | 0.0039571 | 0.98324 | 3.0437e-06 | 0.65041 | 47443.1506 | 0.23299 | 0.89663 | 0.092299 |  | 0.10809
0.28481 | 4.018e-07 | 0.58908 | 18306.9687 | 0.30738 | 0.84199 | 0.0086583 |  | 0.72412 | 1.1044e-07 | 0.63143 | 46963.5296 | 0.45119 | 0.91002 | 0.0032304 | 0.037571 | 4.0524e-07 | 0.33446 | 40314.7266 | 0.48194 | 0.92839 | 0.010126 |  | 0.022014
0.30088 | 4.1848e-07 | 0.69771 | 19410.4165 | 0.86691 | 0.9243 | 0.0065288 |  | 0.96337 | 2.4275e-07 | 0.074307 | 32896.1577 | 0.29246 | 0.89045 | 0.005885 | 0.94213 | 2.457e-06 | 0.64553 | 47318.4322 | 0.68765 | 0.9484 | 0.066238 |  | 0.078652
0.68364 | 8.9954e-07 | 0.0022247 | 9908.2057 | 0.70738 | 0.89953 | 0.011926 |  | 0.52675 | 7.167e-08 | 0.25886 | 38585.232 | 0.074646 | 0.84177 | 0.0021574 | 0.48769 | 1.1786e-06 | 0.81371 | 52487.3247 | 0.039551 | 0.83621 | 0.042776 |  | 0.056859
0.42645 | 5.5304e-07 | 0.69372 | 19366.2169 | 0.45075 | 0.86452 | 0.011193 |  | 0.52846 | 7.1942e-08 | 0.003232 | 25472.3116 | 0.71316 | 0.93688 | 0.0012562 | 0.94734 | 2.5035e-06 | 0.70917 | 49030.3644 | 0.2076 | 0.89216 | 0.078405 |  | 0.090854
0.66926 | 8.7538e-07 | 0.17123 | 14474.3458 | 0.32052 | 0.84427 | 0.017291 |  | 0.56637 | 7.817e-08 | 0.081993 | 33244.4296 | 0.75015 | 0.94072 | 0.0016283 | 0.63552 | 1.4257e-06 | 0.84937 | 54000.4107 | 0.61244 | 0.94128 | 0.043569 |  | 0.062487
0.75832 | 1.0422e-06 | 0.98023 | 26415.7378 | 0.39794 | 0.85673 | 0.024874 |  | 0.21118 | 3.0005e-08 | 0.66756 | 47888.7252 | 0.5269 | 0.91807 | 0.00087493 | 0.39605 | 1.0416e-06 | 0.41512 | 42071.3029 | 0.65004 | 0.94484 | 0.025735 |  | 0.051484
0.070665 | 1.6483e-07 | 0.50657 | 17558.4878 | 0.86455 | 0.92387 | 0.0024362 |  | 0.27181 | 3.7213e-08 | 0.28312 | 39154.9227 | 0.21679 | 0.87853 | 0.001036 | 0.40642 | 1.0568e-06 | 0.74927 | 50233.6369 | 0.68684 | 0.94833 | 0.029956 |  | 0.033428
0.93485 | 1.6824e-06 | 0.95874 | 24766.4683 | 0.2093 | 0.8225 | 0.043296 |  | 0.14273 | 2.1899e-08 | 0.19391 | 36948.6365 | 0.71358 | 0.93692 | 0.00050004 | 0.50787 | 1.2099e-06 | 0.6229 | 46752.391 | 0.061404 | 0.84993 | 0.039946 |  | 0.083742
0.19414 | 3.0752e-07 | 0.45656 | 17122.9897 | 0.59086 | 0.88377 | 0.0054578 |  | 0.31763 | 4.2796e-08 | 0.090301 | 33597.9051 | 0.21505 | 0.87822 | 0.0010879 | 0.10227 | 5.7382e-07 | 0.38941 | 41515.7684 | 0.8821 | 0.96839 | 0.013124 |  | 0.019669
0.82901 | 1.2183e-06 | 0.046194 | 12499.1056 | 0.91005 | 0.93308 | 0.014246 |  | 0.12478 | 1.9733e-08 | 0.42588 | 42303.5033 | 0.64219 | 0.92972 | 0.00050954 | 0.4831 | 1.1716e-06 | 0.87359 | 55199.3628 | 0.77633 | 0.95696 | 0.035361 |  | 0.050116
0.55798 | 7.1198e-07 | 0.45216 | 17085.0814 | 0.1108 | 0.79431 | 0.01766 |  | 0.65614 | 9.4958e-08 | 0.091531 | 33648.4687 | 0.21872 | 0.87886 | 0.0024117 | 0.5626 | 1.2981e-06 | 0.5959 | 46099.0378 | 0.006801 | 0.78625 | 0.047831 |  | 0.067902
0.15261 | 2.6285e-07 | 0.32529 | 15985.0794 | 0.3116 | 0.84273 | 0.0053918 |  | 0.90423 | 1.8122e-07 | 0.7896 | 51585.9222 | 0.22525 | 0.88 | 0.0060185 | 0.1741 | 7.0661e-07 | 0.67377 | 48053.3614 | 0.82924 | 0.9624 | 0.018667 |  | 0.030077
0.86919 | 1.3504e-06 | 0.16347 | 14384.9818 | 0.84796 | 0.9209 | 0.018302 |  | 0.51881 | 7.042e-08 | 0.44432 | 42701.7602 | 0.80341 | 0.94652 | 0.001753 | 0.59892 | 1.3599e-06 | 0.10835 | 34300.855 | 0.22508 | 0.89528 | 0.033356 |  | 0.05341
0.84793 | 1.2765e-06 | 0.02523 | 11834.7083 | 0.28493 | 0.83794 | 0.024451 |  | 0.53706 | 7.3318e-08 | 0.99857 | 79727.672 | 0.74061 | 0.93972 | 0.0031337 | 0.9311 | 2.3699e-06 | 0.36581 | 41003.2247 | 0.50569 | 0.93083 | 0.059587 |  | 0.087172
0.29006 | 4.0725e-07 | 0.58513 | 18269.7972 | 0.30487 | 0.84155 | 0.0087836 |  | 0.38076 | 5.0806e-08 | 0.62704 | 46854.6248 | 0.40605 | 0.90493 | 0.0015002 | 0.69325 | 1.539e-06 | 0.217 | 37553.75 | 0.4758 | 0.92775 | 0.036551 |  | 0.046835
0.5424 | 6.9165e-07 | 0.84278 | 21400.949 | 0.60507 | 0.88568 | 0.013482 |  | 0.47546 | 6.3865e-08 | 0.83949 | 53555.626 | 0.78567 | 0.94454 | 0.0019256 | 0.68143 | 1.5147e-06 | 0.23932 | 38112.5725 | 0.93203 | 0.97516 | 0.031444 |  | 0.046851
0.98804 | 2.4474e-06 | 0.070944 | 13046.0424 | 0.58031 | 0.88236 | 0.039308 |  | 0.53484 | 7.2961e-08 | 0.32184 | 40034.2214 | 0.77571 | 0.94345 | 0.0017393 | 0.189 | 7.313e-07 | 0.92583 | 58635.0814 | 0.77059 | 0.95639 | 0.023299 |  | 0.064346
0.98011 | 2.2224e-06 | 0.25007 | 15292.9273 | 0.47757 | 0.86833 | 0.040389 |  | 0.52307 | 7.1089e-08 | 0.70537 | 48922.0828 | 0.1878 | 0.87313 | 0.0023084 | 0.43036 | 1.0921e-06 | 0.71698 | 49255.5573 | 0.57207 | 0.9374 | 0.031203 |  | 0.0739
0.1026 | 2.0552e-07 | 0.10188 | 13572.7646 | 0.20782 | 0.82216 | 0.0043484 |  | 0.24705 | 3.4253e-08 | 0.64192 | 47227.0343 | 0.35739 | 0.89908 | 0.00103 | 0.012155 | 2.8465e-07 | 0.8938 | 56353.6733 | 0.25856 | 0.90077 | 0.0096991 |  | 0.015078
0.23701 | 3.5233e-07 | 0.64604 | 18862.4801 | 0.95104 | 0.94397 | 0.0048659 |  | 0.479 | 6.4384e-08 | 0.40868 | 41932.3038 | 0.54001 | 0.91942 | 0.0016956 | 0.367 | 9.9919e-07 | 0.72176 | 49395.6035 | 0.13881 | 0.87733 | 0.032388 |  | 0.038949
0.91899 | 1.5802e-06 | 0.70153 | 19453.0541 | 0.25826 | 0.83286 | 0.035937 |  | 0.010598 | 3.4097e-09 | 0.88057 | 55579.5143 | 0.034908 | 0.81887 | 0.00013169 | 0.76755 | 1.7103e-06 | 0.62438 | 46788.9966 | 0.56084 | 0.93631 | 0.047006 |  | 0.083075
0.84296 | 1.2606e-06 | 0.25483 | 15338.5419 | 0.13236 | 0.8018 | 0.029639 |  | 0.49698 | 6.7064e-08 | 0.18143 | 36607.7843 | 0.33634 | 0.8964 | 0.001709 | 0.38548 | 1.0262e-06 | 0.86081 | 54545.8293 | 0.80187 | 0.95954 | 0.030491 |  | 0.061839
0.052592 | 1.3914e-07 | 0.72241 | 19692.7057 | 0.79114 | 0.91166 | 0.0023258 |  | 0.45771 | 6.1297e-08 | 0.47912 | 43457.0207 | 0.72194 | 0.93778 | 0.0015831 | 0.058737 | 4.7076e-07 | 0.30734 | 39708.4324 | 0.56843 | 0.93705 | 0.011354 |  | 0.015263
0.59467 | 7.6199e-07 | 0.96716 | 25288.7852 | 0.029559 | 0.74504 | 0.024197 |  | 0.33037 | 4.4378e-08 | 0.86263 | 54635.6338 | 0.55703 | 0.92116 | 0.0014232 | 0.75248 | 1.6725e-06 | 0.38102 | 41333.9173 | 0.17953 | 0.88668 | 0.047252 |  | 0.072872
0.3849 | 5.0732e-07 | 0.19524 | 14738.9895 | 0.88249 | 0.92728 | 0.0066985 |  | 0.73439 | 1.1307e-07 | 0.74916 | 50229.9505 | 0.46689 | 0.91174 | 0.0034632 | 0.77941 | 1.7414e-06 | 0.83867 | 53519.5119 | 0.58958 | 0.93909 | 0.053054 |  | 0.063216
0.086525 | 1.8561e-07 | 0.61758 | 18579.7021 | 0.81463 | 0.91534 | 0.0029549 |  | 0.62203 | 8.8182e-08 | 0.74479 | 50092.9142 | 0.52299 | 0.91767 | 0.0026628 | 0.093366 | 5.5485e-07 | 0.081438 | 33220.0141 | 0.93512 | 0.97564 | 0.010176 |  | 0.015793
0.64274 | 8.3294e-07 | 0.27901 | 15566.0106 | 0.89184 | 0.92916 | 0.011192 |  | 0.045087 | 9.3262e-09 | 0.38695 | 41462.4675 | 0.16523 | 0.86845 | 0.00027538 | 0.55125 | 1.2794e-06 | 0.7792 | 51220.6457 | 0.8772 | 0.9678 | 0.035319 |  | 0.046786
0.42177 | 5.4781e-07 | 0.97337 | 25759.726 | 0.23392 | 0.8279 | 0.0141 |  | 0.57043 | 7.8863e-08 | 0.94873 | 60871.7895 | 0.34683 | 0.89775 | 0.0028612 | 0.2824 | 8.7544e-07 | 0.54707 | 44965.5217 | 0.64549 | 0.94441 | 0.022851 |  | 0.039812
0.46621 | 5.9844e-07 | 0.41507 | 16765.748 | 0.83941 | 0.91943 | 0.0088364 |  | 0.61813 | 8.7442e-08 | 0.43294 | 42455.8804 | 0.53559 | 0.91897 | 0.0023265 | 0.66714 | 1.4861e-06 | 0.51788 | 44310.0237 | 0.054257 | 0.846 | 0.047902 |  | 0.059065
0.51521 | 6.573e-07 | 0.17665 | 14535.6396 | 0.16361 | 0.81109 | 0.014752 |  | 0.089782 | 1.5386e-08 | 0.60106 | 46222.3547 | 0.13217 | 0.86059 | 0.00049391 | 0.53367 | 1.2508e-06 | 0.79439 | 51758.665 | 0.21571 | 0.89363 | 0.040583 |  | 0.055829
0.15246 | 2.6269e-07 | 0.5504 | 17949.7929 | 0.16047 | 0.81022 | 0.0062773 |  | 0.42446 | 5.6648e-08 | 0.85186 | 54116.3633 | 0.32483 | 0.89489 | 0.0018932 | 0.831 | 1.8949e-06 | 0.38276 | 41371.6985 | 0.10797 | 0.86856 | 0.055864 |  | 0.064035
0.77608 | 1.0817e-06 | 0.95147 | 24388.4518 | 0.47597 | 0.8681 | 0.023948 |  | 0.010749 | 3.4429e-09 | 0.35986 | 40873.2591 | 0.71611 | 0.93718 | 8.4886e-05 | 0.7918 | 1.7754e-06 | 0.98022 | 66281.0556 | 0.95261 | 0.97861 | 0.060906 |  | 0.084938
0.26933 | 3.8578e-07 | 0.75702 | 20117.5746 | 0.43379 | 0.86207 | 0.0080067 |  | 0.72756 | 1.1131e-07 | 0.6404 | 47188.5564 | 0.75132 | 0.94084 | 0.0030477 | 0.83267 | 1.9005e-06 | 0.17229 | 36350.7135 | 0.60828 | 0.94088 | 0.042343 |  | 0.053397
0.64703 | 8.3965e-07 | 0.17415 | 14507.5489 | 0.97133 | 0.9516 | 0.009356 |  | 0.10164 | 1.6883e-08 | 0.83819 | 53498.5094 | 0.49283 | 0.91451 | 0.00053943 | 0.097557 | 5.6389e-07 | 0.14085 | 35408.3203 | 0.42141 | 0.92189 | 0.013062 |  | 0.022957
0.71602 | 9.5748e-07 | 0.3937 | 16581.8045 | 0.38723 | 0.85509 | 0.018942 |  | 0.258 | 3.5559e-08 | 0.28941 | 39299.9002 | 0.64055 | 0.92955 | 0.00086895 | 0.48582 | 1.1758e-06 | 0.73096 | 49669.4704 | 0.86595 | 0.96648 | 0.031674 |  | 0.051485
0.78752 | 1.1086e-06 | 0.068333 | 12995.2026 | 0.8999 | 0.93085 | 0.01342 |  | 0.34797 | 4.6591e-08 | 0.81403 | 52500.0921 | 0.34372 | 0.89735 | 0.0015164 | 0.096483 | 5.6159e-07 | 0.7431 | 50040.3489 | 0.12723 | 0.87425 | 0.018471 |  | 0.033407
0.36213 | 4.8284e-07 | 0.30121 | 15769.2038 | 0.6744 | 0.895 | 0.0078484 |  | 0.61918 | 8.7641e-08 | 0.40503 | 41853.4389 | 0.13782 | 0.86204 | 0.0026402 | 0.59396 | 1.3513e-06 | 0.2017 | 37156.3359 | 0.61283 | 0.94131 | 0.030578 |  | 0.041067
0.92076 | 1.5906e-06 | 0.55499 | 17991.5384 | 0.96254 | 0.94797 | 0.020813 |  | 0.65465 | 9.4649e-08 | 0.53101 | 44603.2956 | 0.82433 | 0.94892 | 0.0024265 | 0.69465 | 1.542e-06 | 0.51473 | 44240.0639 | 0.31272 | 0.90861 | 0.043336 |  | 0.066575
0.33024 | 4.4912e-07 | 0.057467 | 12768.297 | 0.17574 | 0.81433 | 0.0096396 |  | 0.59775 | 8.3673e-08 | 0.63186 | 46974.4618 | 0.17216 | 0.86994 | 0.002663 | 0.21692 | 7.7596e-07 | 0.61885 | 46653.0314 | 0.54309 | 0.93457 | 0.021364 |  | 0.033666
0.01025 | 5.7267e-08 | 0.95444 | 24536.3602 | 0.93468 | 0.93916 | 0.00096504 |  | 0.45201 | 6.0486e-08 | 0.33125 | 40243.6925 | 0.35073 | 0.89824 | 0.0016324 | 0.83711 | 1.9156e-06 | 0.57923 | 45706.0232 | 0.2441 | 0.89847 | 0.056369 |  | 0.058967
0.70458 | 9.3641e-07 | 0.58267 | 18246.7899 | 0.28721 | 0.83836 | 0.020421 |  | 0.71763 | 1.0882e-07 | 0.11998 | 34716.7853 | 0.83467 | 0.95015 | 0.00227 | 0.85393 | 1.976e-06 | 0.44828 | 42787.3967 | 0.90522 | 0.97133 | 0.046024 |  | 0.068715
0.12684 | 2.3399e-07 | 0.00045552 | 9015.2308 | 0.78046 | 0.91004 | 0.0028039 |  | 0.22679 | 3.185e-08 | 0.42879 | 42366.2667 | 0.61445 | 0.92694 | 0.00082922 | 0.83976 | 1.9247e-06 | 0.82331 | 52871.2 | 0.090252 | 0.8625 | 0.067069 |  | 0.070702
0.28124 | 3.9811e-07 | 0.81584 | 20950.715 | 0.78313 | 0.91044 | 0.0069201 |  | 0.5973 | 8.359e-08 | 0.51789 | 44310.3749 | 0.28693 | 0.88966 | 0.0024556 | 0.62488 | 1.4062e-06 | 0.0055012 | 26409.3993 | 0.25346 | 0.89997 | 0.029033 |  | 0.038409
0.17494 | 2.8709e-07 | 0.5628 | 18062.8846 | 0.39589 | 0.85642 | 0.0058315 |  | 0.41378 | 5.5194e-08 | 0.73833 | 49893.3902 | 0.90309 | 0.95927 | 0.0015177 | 0.89855 | 2.1715e-06 | 0.86447 | 54727.8803 | 0.20596 | 0.89185 | 0.073565 |  | 0.080915
0.18779 | 3.0079e-07 | 0.37458 | 16416.6364 | 0.39565 | 0.85638 | 0.0058987 |  | 0.74179 | 1.1502e-07 | 0.35891 | 40852.518 | 0.75068 | 0.94078 | 0.002807 | 0.90752 | 2.2197e-06 | 0.39175 | 41566.4452 | 0.15797 | 0.88197 | 0.063638 |  | 0.072344
0.86458 | 1.3335e-06 | 0.15702 | 14309.0142 | 0.26262 | 0.83371 | 0.027379 |  | 0.56553 | 7.8026e-08 | 0.087358 | 33475.1629 | 0.46285 | 0.9113 | 0.0017964 | 0.96228 | 2.6652e-06 | 0.91079 | 57476.3039 | 0.05075 | 0.84391 | 0.10108 |  | 0.13026
0.76355 | 1.0536e-06 | 0.66607 | 19068.9456 | 0.27648 | 0.83637 | 0.023503 |  | 0.99028 | 3.2554e-07 | 0.97546 | 65094.5566 | 0.54338 | 0.91976 | 0.012033 | 0.7448 | 1.654e-06 | 0.48331 | 43548.5483 | 0.79891 | 0.95924 | 0.040452 |  | 0.075988
0.2985 | 4.16e-07 | 0.86836 | 21888.9116 | 0.95368 | 0.94483 | 0.0063121 |  | 0.96755 | 2.504e-07 | 0.56143 | 45293.4461 | 0.18621 | 0.87281 | 0.0077394 | 0.40796 | 1.0591e-06 | 0.76075 | 50601.9409 | 0.75198 | 0.95457 | 0.029793 |  | 0.043845
0.65147 | 8.4663e-07 | 0.3662 | 16343.9781 | 0.077399 | 0.77994 | 0.021717 |  | 0.6016 | 8.4371e-08 | 0.99512 | 73636.8583 | 0.15348 | 0.86582 | 0.0036813 | 0.88485 | 2.1046e-06 | 0.73923 | 49920.9536 | 0.44652 | 0.92464 | 0.062466 |  | 0.087864
0.99461 | 2.7945e-06 | 0.034772 | 12173.6099 | 0.91647 | 0.93457 | 0.031915 |  | 0.51725 | 7.0176e-08 | 0.9239 | 58475.4681 | 0.082686 | 0.84502 | 0.0026865 | 0.052667 | 4.5354e-07 | 0.27531 | 38973.3482 | 0.23432 | 0.89685 | 0.012025 |  | 0.046626
0.75088 | 1.0264e-06 | 0.41828 | 16793.3948 | 0.86706 | 0.92433 | 0.01477 |  | 0.43037 | 5.746e-08 | 0.46795 | 43213.8495 | 0.4493 | 0.90982 | 0.0015835 | 0.12363 | 6.165e-07 | 0.59598 | 46101.1516 | 0.88094 | 0.96825 | 0.015474 |  | 0.031828
0.43185 | 5.591e-07 | 0.27796 | 15556.2648 | 0.49447 | 0.87069 | 0.01012 |  | 0.44563 | 5.9585e-08 | 0.47303 | 43324.3711 | 0.016887 | 0.79863 | 0.0020819 | 0.68508 | 1.5222e-06 | 0.23171 | 37924.5799 | 0.32752 | 0.91058 | 0.038206 |  | 0.050407
0.93464 | 1.6809e-06 | 0.095469 | 13472.9272 | 0.32674 | 0.84533 | 0.032347 |  | 0.90111 | 1.7914e-07 | 0.44465 | 42708.9235 | 0.75125 | 0.94084 | 0.0045274 | 0.87275 | 2.0511e-06 | 0.26034 | 38620.5545 | 0.80223 | 0.95958 | 0.045269 |  | 0.082143
0.52555 | 6.7021e-07 | 0.79749 | 20672.0384 | 0.08569 | 0.78393 | 0.018116 |  | 0.46794 | 6.2769e-08 | 0.47069 | 43273.4722 | 0.12103 | 0.85757 | 0.0019478 | 0.64298 | 1.4397e-06 | 0.046315 | 31371.7607 | 0.26101 | 0.90115 | 0.032817 |  | 0.052881
0.71885 | 9.6279e-07 | 0.45392 | 17100.1994 | 0.15857 | 0.80969 | 0.022716 |  | 0.68531 | 1.0123e-07 | 0.35266 | 40715.8119 | 0.7933 | 0.94538 | 0.0024327 | 0.43204 | 1.0946e-06 | 0.41722 | 42116.5863 | 0.3536 | 0.91391 | 0.029322 |  | 0.054471
0.69115 | 9.1252e-07 | 0.43581 | 16944.1637 | 0.14578 | 0.80598 | 0.02174 |  | 0.25421 | 3.5107e-08 | 0.96329 | 62820.1641 | 0.31096 | 0.89303 | 0.0013137 | 0.54259 | 1.2652e-06 | 0.0089019 | 27338.8862 | 0.83989 | 0.96355 | 0.020705 |  | 0.043759
0.58603 | 7.4992e-07 | 0.60367 | 18445.4601 | 0.87 | 0.92488 | 0.011332 |  | 0.068124 | 1.2555e-08 | 0.40618 | 41878.2998 | 0.30585 | 0.89233 | 0.00035301 | 0.92162 | 2.3047e-06 | 0.48047 | 43486.3858 | 0.46537 | 0.92666 | 0.061243 |  | 0.072928
0.54018 | 6.8879e-07 | 0.63008 | 18702.4753 | 0.70281 | 0.8989 | 0.01189 |  | 0.48736 | 6.5621e-08 | 0.21508 | 37504.5418 | 0.062476 | 0.83621 | 0.0019705 | 0.0902 | 5.479e-07 | 0.15955 | 35980.632 | 0.015534 | 0.80885 | 0.017147 |  | 0.031008
0.033219 | 1.0766e-07 | 0.70477 | 19489.5316 | 0.37717 | 0.85353 | 0.0022768 |  | 0.69877 | 1.043e-07 | 0.84712 | 53896.9737 | 0.55733 | 0.92119 | 0.0033094 | 0.23814 | 8.0884e-07 | 0.73567 | 49811.8742 | 0.59688 | 0.93979 | 0.023198 |  | 0.028785
0.13461 | 2.4282e-07 | 0.85697 | 21663.027 | 0.89428 | 0.92967 | 0.0039413 |  | 0.27508 | 3.7608e-08 | 0.8082 | 52273.9978 | 0.72617 | 0.93822 | 0.0011258 | 0.24408 | 8.1792e-07 | 0.35613 | 40791.7435 | 0.96834 | 0.98181 | 0.017682 |  | 0.022749
0.15814 | 2.6891e-07 | 0.79237 | 20597.6375 | 0.73102 | 0.90284 | 0.0047892 |  | 0.87511 | 1.6385e-07 | 0.49279 | 43756.0401 | 0.050901 | 0.82997 | 0.0054157 | 0.12783 | 6.2451e-07 | 0.89346 | 56332.5817 | 0.64594 | 0.94445 | 0.019652 |  | 0.029857
0.9742 | 2.1059e-06 | 0.23028 | 15099.5181 | 0.24689 | 0.83058 | 0.044459 |  | 0.3261 | 4.3847e-08 | 0.33434 | 40312.158 | 0.93143 | 0.96395 | 0.00099039 | 0.65453 | 1.4616e-06 | 0.042537 | 31119.9359 | 0.78125 | 0.95745 | 0.027222 |  | 0.072672
0.61199 | 7.8677e-07 | 0.6123 | 18528.4436 | 0.45251 | 0.86477 | 0.015623 |  | 0.062988 | 1.1859e-08 | 0.90212 | 56882.7522 | 0.87371 | 0.95509 | 0.0003688 | 0.93617 | 2.4083e-06 | 0.88031 | 55565.0095 | 0.55121 | 0.93537 | 0.076218 |  | 0.09221
0.67109 | 8.7841e-07 | 0.63579 | 18759.2949 | 0.81765 | 0.91583 | 0.014023 |  | 0.051375 | 1.0238e-08 | 0.92185 | 58309.4664 | 0.047234 | 0.82773 | 0.00040158 | 0.74931 | 1.6648e-06 | 0.62402 | 46779.972 | 0.7943 | 0.95877 | 0.043347 |  | 0.057772
0.65575 | 8.5344e-07 | 0.36705 | 16351.353 | 0.25248 | 0.83171 | 0.018385 |  | 0.52589 | 7.1533e-08 | 0.24777 | 38318.8922 | 0.752 | 0.94092 | 0.0016598 | 0.8259 | 1.8781e-06 | 0.97088 | 64136.7884 | 0.52392 | 0.93267 | 0.067251 |  | 0.087296
0.30559 | 4.2338e-07 | 0.86997 | 21922.1161 | 0.048905 | 0.76272 | 0.01234 |  | 0.29098 | 3.953e-08 | 0.88446 | 55799.3611 | 0.038089 | 0.82139 | 0.0015244 | 0.56143 | 1.2961e-06 | 0.049432 | 31568.7696 | 0.1481 | 0.87964 | 0.031662 |  | 0.045526
0.45378 | 5.8405e-07 | 0.12668 | 13926.5595 | 0.18966 | 0.81785 | 0.012645 |  | 0.5497 | 7.5379e-08 | 0.038415 | 30826.2977 | 0.73903 | 0.93955 | 0.0014907 | 0.50782 | 1.2099e-06 | 0.97741 | 65551.5483 | 0.046106 | 0.84092 | 0.050206 |  | 0.064343
0.82121 | 1.196e-06 | 0.060341 | 12830.9544 | 0.95517 | 0.94533 | 0.01298 |  | 0.97384 | 2.6395e-07 | 0.92677 | 58714.0866 | 0.59207 | 0.9247 | 0.0089064 | 0.10125 | 5.7171e-07 | 0.42204 | 42220.6595 | 0.064546 | 0.85152 | 0.017713 |  | 0.0396
0.69027 | 9.11e-07 | 0.69761 | 19409.2563 | 0.4701 | 0.86728 | 0.018259 |  | 0.82373 | 1.4097e-07 | 0.044337 | 31241.8257 | 0.92715 | 0.96319 | 0.0025757 | 0.46772 | 1.1481e-06 | 0.72695 | 49549.1504 | 0.10813 | 0.86861 | 0.037922 |  | 0.058757
0.093911 | 1.9488e-07 | 0.96492 | 25139.1694 | 0.11091 | 0.79436 | 0.0054565 |  | 0.44102 | 5.8938e-08 | 0.12899 | 35023.042 | 0.95895 | 0.96963 | 0.0011575 | 0.068082 | 4.9552e-07 | 0.64556 | 47319.3212 | 0.39594 | 0.91899 | 0.01429 |  | 0.020904
0.22565 | 3.4053e-07 | 0.69081 | 19334.1773 | 0.27069 | 0.83527 | 0.0076635 |  | 0.56216 | 7.7456e-08 | 0.39358 | 41606.0058 | 0.91318 | 0.96085 | 0.0018139 | 0.071237 | 5.0347e-07 | 0.38414 | 41401.6879 | 0.41204 | 0.92084 | 0.013089 |  | 0.022566
0.42424 | 5.5056e-07 | 0.47413 | 17275.1204 | 0.7442 | 0.90472 | 0.0088978 |  | 0.22423 | 3.1547e-08 | 0.26202 | 38660.5644 | 0.86504 | 0.95395 | 0.00070899 | 0.39585 | 1.0413e-06 | 0.30711 | 39703.2156 | 0.63045 | 0.94299 | 0.024694 |  | 0.034301
0.30851 | 4.2641e-07 | 0.8238 | 21078.0909 | 0.72675 | 0.90224 | 0.0077064 |  | 0.29292 | 3.9766e-08 | 0.88182 | 55649.4717 | 0.034708 | 0.8187 | 0.0015374 | 0.48023 | 1.1672e-06 | 0.95305 | 61391.7964 | 0.2775 | 0.90364 | 0.042228 |  | 0.051472
0.32193 | 4.4041e-07 | 0.56497 | 18082.7636 | 0.20179 | 0.82076 | 0.010183 |  | 0.24353 | 3.3834e-08 | 0.52357 | 44436.8164 | 0.69012 | 0.93454 | 0.00089656 | 0.60315 | 1.3673e-06 | 0.27811 | 39038.7167 | 0.14152 | 0.87801 | 0.038045 |  | 0.049125
0.90799 | 1.5198e-06 | 0.65165 | 18919.6793 | 0.70073 | 0.89861 | 0.026418 |  | 0.82777 | 1.4252e-07 | 0.37954 | 41301.8977 | 0.16138 | 0.86761 | 0.0042065 | 0.84807 | 1.9543e-06 | 0.85027 | 54041.9312 | 0.70914 | 0.95044 | 0.058674 |  | 0.089299
0.4015 | 5.2539e-07 | 0.077453 | 13167.6282 | 0.25978 | 0.83316 | 0.010561 |  | 0.73426 | 1.1303e-07 | 0.94322 | 60263.1011 | 0.7023 | 0.93577 | 0.003823 | 0.34126 | 9.6172e-07 | 0.15112 | 35727.2405 | 0.94623 | 0.97747 | 0.018691 |  | 0.033074
0.25179 | 3.6764e-07 | 0.62553 | 18657.5905 | 0.74144 | 0.90432 | 0.0061828 |  | 0.55614 | 7.6448e-08 | 0.078732 | 33099.3869 | 0.62379 | 0.92788 | 0.0016569 | 0.15427 | 6.7259e-07 | 0.039034 | 30871.8198 | 0.57133 | 0.93733 | 0.013424 |  | 0.021264
0.42711 | 5.5377e-07 | 0.87039 | 21930.748 | 0.036163 | 0.75198 | 0.016598 |  | 0.076205 | 1.3629e-08 | 0.51173 | 44173.6351 | 0.10867 | 0.85395 | 0.00043142 | 0.5938 | 1.351e-06 | 0.29244 | 39369.4154 | 0.26092 | 0.90113 | 0.035666 |  | 0.052695
0.65063 | 8.453e-07 | 0.71177 | 19569.1597 | 0.85285 | 0.92176 | 0.013417 |  | 0.77495 | 1.2445e-07 | 0.11308 | 34473.3879 | 0.41044 | 0.90544 | 0.0029732 | 0.18635 | 7.2696e-07 | 0.9025 | 56907.868 | 0.19234 | 0.88926 | 0.025446 |  | 0.041837
0.65429 | 8.5111e-07 | 0.36702 | 16351.1019 | 0.73182 | 0.90295 | 0.013519 |  | 0.91921 | 1.9225e-07 | 0.081457 | 33220.8439 | 0.14302 | 0.86333 | 0.0050585 | 0.81582 | 1.8462e-06 | 0.55427 | 45129.6133 | 0.2877 | 0.90512 | 0.05305 |  | 0.071627
0.94096 | 1.7282e-06 | 0.78901 | 20549.6463 | 0.91839 | 0.93502 | 0.026441 |  | 0.8641 | 1.5828e-07 | 0.62833 | 46886.4976 | 0.37675 | 0.90146 | 0.0047113 | 0.54514 | 1.2694e-06 | 0.35684 | 40807.3822 | 0.21712 | 0.89388 | 0.034952 |  | 0.066104
0.2709 | 3.8741e-07 | 0.69842 | 19418.2998 | 0.47502 | 0.86797 | 0.0077454 |  | 0.39631 | 5.2853e-08 | 0.22923 | 37862.6387 | 0.23189 | 0.88112 | 0.001432 | 0.24341 | 8.169e-07 | 0.97915 | 65992.547 | 0.21609 | 0.8937 | 0.031696 |  | 0.040874
0.80412 | 1.1499e-06 | 0.78066 | 20432.5597 | 0.048125 | 0.76214 | 0.032915 |  | 0.882 | 1.6758e-07 | 0.5679 | 45442.7049 | 0.22344 | 0.87969 | 0.0051158 | 0.50346 | 1.2031e-06 | 0.14381 | 35501.3832 | 0.70682 | 0.95022 | 0.025538 |  | 0.063568
0.90646 | 1.512e-06 | 0.73739 | 19871.9495 | 0.69724 | 0.89813 | 0.026985 |  | 0.73772 | 1.1394e-07 | 0.13327 | 35164.2733 | 0.33067 | 0.89566 | 0.0028357 | 0.068392 | 4.963e-07 | 0.93438 | 59387.5264 | 0.1542 | 0.8811 | 0.018154 |  | 0.047975
0.31738 | 4.3566e-07 | 0.91736 | 23098.0799 | 0.084913 | 0.78357 | 0.012202 |  | 0.14285 | 2.1913e-08 | 0.31078 | 39786.0943 | 0.31311 | 0.89332 | 0.00059418 | 0.025415 | 3.5733e-07 | 0.77766 | 51167.4925 | 0.54374 | 0.93463 | 0.01059 |  | 0.023387
0.44097 | 5.6941e-07 | 0.36419 | 16326.4457 | 0.30643 | 0.84182 | 0.011803 |  | 0.91175 | 1.8653e-07 | 0.17126 | 36321.3505 | 0.066438 | 0.83812 | 0.0054843 | 0.96511 | 2.7025e-06 | 0.080452 | 33176.3624 | 0.27277 | 0.90293 | 0.063458 |  | 0.080745
0.27402 | 3.9063e-07 | 0.74722 | 19993.3026 | 0.41378 | 0.85911 | 0.0081759 |  | 0.38885 | 5.1867e-08 | 0.42277 | 42236.2938 | 0.2207 | 0.87921 | 0.0015118 | 0.55911 | 1.2923e-06 | 0.43146 | 42423.8975 | 0.86241 | 0.96607 | 0.030323 |  | 0.040011
0.42543 | 5.519e-07 | 0.78847 | 20542.0016 | 0.55548 | 0.87902 | 0.010832 |  | 0.22995 | 3.2224e-08 | 0.96847 | 63687.3154 | 0.73089 | 0.93871 | 0.0011362 | 0.42418 | 1.083e-06 | 0.40489 | 41850.427 | 0.95313 | 0.97871 | 0.0242 |  | 0.036167
0.31646 | 4.347e-07 | 0.88525 | 22255.1314 | 0.85741 | 0.92257 | 0.0074111 |  | 0.87867 | 1.6575e-07 | 0.87378 | 55209.3747 | 0.28322 | 0.88912 | 0.0056782 | 0.89122 | 2.1348e-06 | 0.034715 | 30542.5898 | 0.9713 | 0.9825 | 0.035303 |  | 0.048393
0.30011 | 4.1767e-07 | 0.15013 | 14226.0024 | 0.097812 | 0.78922 | 0.010057 |  | 0.83553 | 1.4561e-07 | 0.41937 | 42162.933 | 0.18404 | 0.87238 | 0.0043057 | 0.62872 | 1.4132e-06 | 0.61723 | 46613.419 | 0.22472 | 0.89522 | 0.042457 |  | 0.05682
0.48208 | 6.1712e-07 | 0.30349 | 15789.8174 | 0.36318 | 0.85132 | 0.012185 |  | 0.10521 | 1.7328e-08 | 0.60028 | 46203.5823 | 0.85617 | 0.95281 | 0.00045305 | 0.81268 | 1.8365e-06 | 0.14659 | 35588.181 | 0.28277 | 0.90441 | 0.044934 |  | 0.057572
0.77041 | 1.0688e-06 | 0.34741 | 16180.0948 | 0.66919 | 0.8943 | 0.017629 |  | 0.23055 | 3.2294e-08 | 0.83136 | 53205.3614 | 0.21087 | 0.87747 | 0.0011005 | 0.33586 | 9.5385e-07 | 0.72912 | 49614.0745 | 0.97257 | 0.9828 | 0.024692 |  | 0.043422
0.52228 | 6.6611e-07 | 0.36641 | 16345.8051 | 0.35125 | 0.8494 | 0.013412 |  | 0.04472 | 9.2722e-09 | 0.77758 | 51164.8506 | 0.47009 | 0.91208 | 0.00028776 | 0.12175 | 6.1289e-07 | 0.52373 | 44440.3006 | 0.48984 | 0.92921 | 0.016455 |  | 0.030155
0.82763 | 1.2142e-06 | 0.15647 | 14302.4825 | 0.076236 | 0.77935 | 0.030237 |  | 0.62601 | 8.8945e-08 | 0.8269 | 53018.5939 | 0.83824 | 0.95058 | 0.0026264 | 0.85749 | 1.9895e-06 | 0.24767 | 38316.305 | 0.27792 | 0.9037 | 0.051228 |  | 0.084092
0.87301 | 1.3648e-06 | 0.85131 | 21556.0449 | 0.33424 | 0.84659 | 0.030795 |  | 0.11281 | 1.8269e-08 | 0.55731 | 45198.9722 | 0.078447 | 0.84334 | 0.00059889 | 0.0155 | 3.0642e-07 | 0.86722 | 54867.2565 | 0.81004 | 0.96038 | 0.0091366 |  | 0.04053
0.61278 | 7.8792e-07 | 0.94719 | 24188.8732 | 0.28504 | 0.83796 | 0.019169 |  | 0.33585 | 4.5064e-08 | 0.19544 | 36989.6809 | 0.70112 | 0.93565 | 0.0010338 | 0.10441 | 5.7829e-07 | 0.32228 | 40044.0351 | 0.18189 | 0.88716 | 0.015988 |  | 0.036191
0.60887 | 7.8225e-07 | 0.79971 | 20704.7675 | 0.32354 | 0.84479 | 0.017477 |  | 0.87052 | 1.6148e-07 | 0.70111 | 48801.5851 | 0.98341 | 0.97714 | 0.0041735 | 0.33157 | 9.4759e-07 | 0.016634 | 28688.0347 | 0.90324 | 0.97107 | 0.015601 |  | 0.037251
0.55982 | 7.1441e-07 | 0.76088 | 20167.5051 | 0.6621 | 0.89334 | 0.013111 |  | 0.54577 | 7.4734e-08 | 0.2536 | 38459.4253 | 0.037962 | 0.8213 | 0.0023502 | 0.37653 | 1.0131e-06 | 0.17256 | 36358.4526 | 0.66788 | 0.94653 | 0.022178 |  | 0.037639
0.14371 | 2.5301e-07 | 0.0067587 | 10678.975 | 0.63239 | 0.88934 | 0.0036542 |  | 0.54718 | 7.4964e-08 | 0.69583 | 48653.8998 | 0.67921 | 0.93343 | 0.0021394 | 0.29483 | 8.938e-07 | 0.39755 | 41691.8083 | 0.75035 | 0.95441 | 0.021352 |  | 0.027146
0.6201 | 7.9866e-07 | 0.22001 | 14996.3919 | 0.11396 | 0.79548 | 0.019072 |  | 0.61292 | 8.6463e-08 | 0.20149 | 37150.6812 | 0.23481 | 0.88161 | 0.0023126 | 0.75727 | 1.6843e-06 | 0.92031 | 58187.634 | 0.65262 | 0.94509 | 0.054415 |  | 0.0758
0.83889 | 1.2479e-06 | 0.10299 | 13589.5392 | 0.13425 | 0.80241 | 0.028404 |  | 0.63347 | 9.0393e-08 | 0.41409 | 42049.0649 | 0.57566 | 0.92305 | 0.0023636 | 0.64468 | 1.4429e-06 | 0.92597 | 58646.8696 | 0.96683 | 0.98147 | 0.043868 |  | 0.074635
0.00060747 | 1.342e-08 | 0.44773 | 17046.836 | 0.51271 | 0.87321 | 0.00024894 |  | 0.8026 | 1.3335e-07 | 0.99268 | 71556.8411 | 0.32032 | 0.89429 | 0.0055015 | 0.57343 | 1.3162e-06 | 0.19423 | 36957.2011 | 0.97859 | 0.98438 | 0.025743 |  | 0.031493
0.58077 | 7.4266e-07 | 0.073116 | 13087.4049 | 0.75023 | 0.90558 | 0.010543 |  | 0.28898 | 3.9288e-08 | 0.27108 | 38874.3484 | 0.79578 | 0.94566 | 0.00090917 | 0.57488 | 1.3186e-06 | 0.23082 | 37902.359 | 0.70573 | 0.95012 | 0.029505 |  | 0.040958
0.19132 | 3.0454e-07 | 0.55579 | 17998.8266 | 0.42564 | 0.86087 | 0.0060709 |  | 0.42712 | 5.7013e-08 | 0.15006 | 35694.9946 | 0.4498 | 0.90987 | 0.001376 | 0.41181 | 1.0647e-06 | 0.43296 | 42456.3024 | 0.6249 | 0.94246 | 0.026669 |  | 0.034116
0.31671 | 4.3496e-07 | 0.3254 | 15986.0274 | 0.16831 | 0.81237 | 0.0099736 |  | 0.87941 | 1.6616e-07 | 0.1696 | 36273.8813 | 0.77821 | 0.94372 | 0.0036631 | 0.14721 | 6.601e-07 | 0.81085 | 52376.3006 | 0.28116 | 0.90417 | 0.021171 |  | 0.034808
0.83922 | 1.2489e-06 | 0.77794 | 20395.135 | 0.59684 | 0.88457 | 0.023894 |  | 0.3553 | 4.7523e-08 | 0.12035 | 34729.6151 | 0.5895 | 0.92444 | 0.0010774 | 0.21136 | 7.672e-07 | 0.94545 | 60502.6286 | 0.91892 | 0.97322 | 0.024387 |  | 0.049359
0.96173 | 1.9276e-06 | 0.64022 | 18803.6847 | 0.57364 | 0.88146 | 0.035991 |  | 0.37066 | 4.9494e-08 | 0.53453 | 44682.3873 | 0.91204 | 0.96067 | 0.0012328 | 0.43884 | 1.1048e-06 | 0.52287 | 44421.2246 | 0.55203 | 0.93545 | 0.029201 |  | 0.066424
0.2107 | 3.2492e-07 | 0.60473 | 18455.5435 | 0.304 | 0.84139 | 0.0070372 |  | 0.73966 | 1.1445e-07 | 0.53216 | 44629.106 | 0.68552 | 0.93407 | 0.0030466 | 0.49003 | 1.1822e-06 | 0.48366 | 43556.0566 | 0.90917 | 0.97186 | 0.027936 |  | 0.03802
0.0022136 | 2.5898e-08 | 0.015119 | 11345.8818 | 0.552 | 0.87855 | 0.0004046 |  | 0.039116 | 8.4315e-09 | 0.52684 | 44509.9442 | 0.1742 | 0.87037 | 0.00025907 | 0.4105 | 1.0628e-06 | 0.63638 | 47087.4241 | 0.6469 | 0.94455 | 0.028798 |  | 0.029462
0.59738 | 7.6581e-07 | 0.62143 | 18617.3273 | 0.72184 | 0.90155 | 0.013032 |  | 0.19098 | 2.7622e-08 | 0.004964 | 26221.4853 | 0.48958 | 0.91417 | 0.00053875 | 0.58847 | 1.3418e-06 | 0.21742 | 37564.39 | 0.53986 | 0.93425 | 0.031273 |  | 0.044844
0.51446 | 6.5636e-07 | 0.64635 | 18865.606 | 0.46971 | 0.86722 | 0.013004 |  | 0.75796 | 1.1947e-07 | 0.4921 | 43740.9049 | 0.60174 | 0.92567 | 0.0031966 | 0.63563 | 1.4259e-06 | 0.079067 | 33114.4459 | 0.23268 | 0.89658 | 0.034086 |  | 0.050287
0.56467 | 7.2087e-07 | 0.99082 | 28046.7051 | 0.26747 | 0.83465 | 0.018879 |  | 0.3646 | 4.8713e-08 | 0.044121 | 31227.3719 | 0.42131 | 0.90668 | 0.0010878 | 0.75723 | 1.6842e-06 | 0.46313 | 43109.0897 | 0.29165 | 0.90569 | 0.046794 |  | 0.066761
0.71778 | 9.6078e-07 | 0.37014 | 16378.123 | 0.11606 | 0.79624 | 0.023414 |  | 0.66663 | 9.7159e-08 | 0.89278 | 56291.1873 | 0.60175 | 0.92567 | 0.003164 | 0.62122 | 1.3995e-06 | 0.45635 | 42962.0435 | 0.71531 | 0.95103 | 0.034594 |  | 0.061173
0.14715 | 2.5683e-07 | 0.79646 | 20656.9254 | 0.16505 | 0.81149 | 0.0063939 |  | 0.34384 | 4.6069e-08 | 0.95505 | 61647.4787 | 0.86026 | 0.95333 | 0.0015421 | 0.92195 | 2.3068e-06 | 0.59153 | 45995.5016 | 0.46803 | 0.92694 | 0.06394 |  | 0.071876
0.45336 | 5.8356e-07 | 0.73002 | 19782.9524 | 0.52053 | 0.87428 | 0.011474 |  | 0.41727 | 5.5667e-08 | 0.44055 | 42620.3153 | 0.9247 | 0.96276 | 0.0013237 | 0.51726 | 1.2247e-06 | 0.72414 | 49465.6775 | 0.21216 | 0.89299 | 0.03853 |  | 0.051327
0.036841 | 1.1399e-07 | 0.0088079 | 10886.517 | 0.96069 | 0.94729 | 0.0011142 |  | 0.41682 | 5.5606e-08 | 0.50437 | 44010.8738 | 0.58817 | 0.92431 | 0.0014997 | 0.71259 | 1.5804e-06 | 0.87332 | 55184.6893 | 0.88284 | 0.96848 | 0.046594 |  | 0.049208
0.70966 | 9.4568e-07 | 0.50515 | 17546.0156 | 0.69539 | 0.89787 | 0.01591 |  | 0.94677 | 2.1903e-07 | 0.34098 | 40458.9821 | 0.30872 | 0.89272 | 0.0060139 | 0.65936 | 1.4709e-06 | 0.046793 | 31402.5378 | 0.47927 | 0.92811 | 0.030697 |  | 0.052621
0.33236 | 4.5135e-07 | 0.056321 | 12742.7095 | 0.53421 | 0.87614 | 0.0074167 |  | 0.949 | 2.2177e-07 | 0.17546 | 36440.4938 | 0.40116 | 0.90436 | 0.0055121 | 0.72474 | 1.6074e-06 | 0.64834 | 47390.1362 | 0.057063 | 0.8476 | 0.053741 |  | 0.06667
0.059562 | 1.4937e-07 | 0.060366 | 12831.5002 | 0.92772 | 0.93733 | 0.0017183 |  | 0.050087 | 1.0054e-08 | 0.86457 | 54732.5075 | 0.38947 | 0.90299 | 0.00033389 | 0.87486 | 2.0601e-06 | 0.24467 | 38243.3704 | 0.32678 | 0.91049 | 0.05202 |  | 0.054072
0.50393 | 6.4343e-07 | 0.69011 | 19326.51 | 0.028837 | 0.7442 | 0.019045 |  | 0.073831 | 1.3316e-08 | 0.14595 | 35568.3368 | 0.029117 | 0.81368 | 0.00041002 | 0.47095 | 1.153e-06 | 0.26878 | 38820.2688 | 0.26626 | 0.90195 | 0.03009 |  | 0.049545
0.14616 | 2.5573e-07 | 0.99228 | 28407.5693 | 0.53185 | 0.87582 | 0.0059632 |  | 0.98635 | 3.0453e-07 | 0.078177 | 33074.2907 | 0.2782 | 0.88839 | 0.0074515 | 0.59222 | 1.3483e-06 | 0.77099 | 50940.7918 | 0.83202 | 0.9627 | 0.037465 |  | 0.05088
0.66322 | 8.6548e-07 | 0.26563 | 15441.0561 | 0.40797 | 0.85824 | 0.016482 |  | 0.22118 | 3.1186e-08 | 0.4335 | 42467.9038 | 0.4527 | 0.91019 | 0.00084808 | 0.9168 | 2.2742e-06 | 0.80356 | 52097.8821 | 0.99957 | 0.99617 | 0.059777 |  | 0.077107
0.31797 | 4.3627e-07 | 0.22656 | 15062.3529 | 0.26276 | 0.83374 | 0.0090934 |  | 0.73223 | 1.1251e-07 | 0.63569 | 47070.0669 | 0.38362 | 0.90229 | 0.0033521 | 0.14912 | 6.635e-07 | 0.88093 | 55599.3195 | 0.46249 | 0.92635 | 0.021367 |  | 0.033813
0.97194 | 2.0683e-06 | 0.35524 | 16248.4909 | 0.49265 | 0.87044 | 0.0381 |  | 0.29254 | 3.9721e-08 | 0.57597 | 45629.9437 | 0.30998 | 0.89289 | 0.0011818 | 0.0032067 | 1.9316e-07 | 0.45552 | 42944.1621 | 0.065513 | 0.852 | 0.0060379 |  | 0.04532
0.19997 | 3.1366e-07 | 0.74121 | 19918.7344 | 0.032773 | 0.74857 | 0.0092469 |  | 0.41341 | 5.5144e-08 | 0.29985 | 39538.5764 | 0.45194 | 0.91011 | 0.0014264 | 0.49205 | 1.1853e-06 | 0.14949 | 35677.3456 | 0.62812 | 0.94277 | 0.025878 |  | 0.036551
0.62563 | 8.0688e-07 | 0.11721 | 13796.7561 | 0.78889 | 0.91132 | 0.011341 |  | 0.35446 | 4.7416e-08 | 0.2085 | 37334.4659 | 0.13394 | 0.86105 | 0.0013393 | 0.073794 | 5.0978e-07 | 0.64764 | 47372.3139 | 0.95381 | 0.97883 | 0.012764 |  | 0.025445
0.48304 | 6.1826e-07 | 0.884 | 22226.5912 | 0.72674 | 0.90224 | 0.011494 |  | 0.71476 | 1.0812e-07 | 0.22229 | 37688.2245 | 0.026243 | 0.81075 | 0.0034442 | 0.93156 | 2.3733e-06 | 0.17625 | 36462.7647 | 0.95594 | 0.97923 | 0.046688 |  | 0.061626
0.38719 | 5.098e-07 | 0.64402 | 18842.0163 | 0.62853 | 0.88882 | 0.0092341 |  | 0.18495 | 2.6912e-08 | 0.96084 | 62448.7682 | 0.73265 | 0.93889 | 0.00093301 | 0.30354 | 9.0661e-07 | 0.069152 | 32649.0836 | 0.82041 | 0.96146 | 0.01729 |  | 0.027457
0.048227 | 1.325e-07 | 0.83819 | 21320.2608 | 0.84033 | 0.91958 | 0.0022322 |  | 0.81157 | 1.3649e-07 | 0.71653 | 49242.5084 | 0.68186 | 0.9337 | 0.0039304 | 0.13476 | 6.3747e-07 | 0.56229 | 45313.3438 | 0.16078 | 0.88262 | 0.019303 |  | 0.025465
0.29863 | 4.1614e-07 | 0.30724 | 15823.6711 | 0.71855 | 0.90108 | 0.0065726 |  | 0.84441 | 1.4931e-07 | 0.94452 | 60402.0749 | 0.38941 | 0.90298 | 0.0053408 | 0.66641 | 1.4847e-06 | 0.48992 | 43693.2366 | 0.12741 | 0.8743 | 0.044706 |  | 0.05662
0.50488 | 6.4459e-07 | 0.95635 | 24636.1386 | 0.75596 | 0.90642 | 0.012481 |  | 0.28891 | 3.9279e-08 | 0.16237 | 36063.8636 | 0.81947 | 0.94836 | 0.00084939 | 0.82975 | 1.8908e-06 | 0.55936 | 45246.0528 | 0.60532 | 0.9406 | 0.050073 |  | 0.063404
0.6758 | 8.8626e-07 | 0.74836 | 20007.587 | 0.81843 | 0.91595 | 0.014646 |  | 0.98821 | 3.1358e-07 | 0.50107 | 43938.0177 | 0.096175 | 0.84991 | 0.0099781 | 0.1536 | 6.7142e-07 | 0.90778 | 57264.9605 | 0.25593 | 0.90036 | 0.02317 |  | 0.047794
0.27932 | 3.9611e-07 | 0.72813 | 19760.33 | 0.012799 | 0.71781 | 0.012601 |  | 0.5731 | 7.9321e-08 | 0.26011 | 38615.0421 | 0.24837 | 0.88382 | 0.0021609 | 0.96985 | 2.7716e-06 | 0.83094 | 53187.5308 | 0.9764 | 0.98378 | 0.076451 |  | 0.091213
0.088978 | 1.8872e-07 | 0.54217 | 17875.3782 | 0.74188 | 0.90438 | 0.0031061 |  | 0.75373 | 1.1828e-07 | 0.57894 | 45699.1978 | 0.98416 | 0.97746 | 0.0028753 | 0.64023 | 1.4345e-06 | 0.74108 | 49977.8216 | 0.52358 | 0.93263 | 0.041897 |  | 0.047879
0.36604 | 4.8703e-07 | 0.36579 | 16340.384 | 0.60643 | 0.88586 | 0.0083947 |  | 0.78186 | 1.2658e-07 | 0.40189 | 41785.718 | 0.88587 | 0.95676 | 0.0030096 | 0.98108 | 2.9884e-06 | 0.56482 | 45371.4552 | 0.91372 | 0.97249 | 0.073131 |  | 0.084536
0.8614 | 1.3221e-06 | 0.32506 | 15982.9692 | 0.25539 | 0.83229 | 0.028218 |  | 0.53302 | 7.2669e-08 | 0.59855 | 46162.4297 | 0.20446 | 0.8763 | 0.0022573 | 0.13686 | 6.4135e-07 | 0.17193 | 36340.4609 | 0.71897 | 0.95138 | 0.013818 |  | 0.044294
0.53952 | 6.8795e-07 | 0.901 | 22639.6004 | 0.26786 | 0.83473 | 0.01646 |  | 0.26177 | 3.6009e-08 | 0.73675 | 49844.9666 | 0.19292 | 0.87412 | 0.0011815 | 0.12939 | 6.2745e-07 | 0.53817 | 44764.2471 | 0.3029 | 0.90727 | 0.017838 |  | 0.03548
0.37409 | 4.9565e-07 | 0.48247 | 17347.5895 | 0.1786 | 0.81507 | 0.011534 |  | 0.55901 | 7.6927e-08 | 0.9618 | 62592.5619 | 0.89136 | 0.95754 | 0.0025914 | 0.17353 | 7.0567e-07 | 0.029504 | 30102.8322 | 0.14383 | 0.87859 | 0.016837 |  | 0.030962
0.30342 | 4.2111e-07 | 0.11011 | 13695.3607 | 0.68318 | 0.8962 | 0.0064135 |  | 0.61703 | 8.7234e-08 | 0.93699 | 59634.5397 | 0.20868 | 0.87707 | 0.0032207 | 6.4128e-05 | 6.7314e-08 | 0.39798 | 41701.1437 | 0.3816 | 0.91731 | 0.0017751 |  | 0.011409
0.28861 | 4.0575e-07 | 0.402 | 16653.32 | 0.42709 | 0.86109 | 0.0078467 |  | 0.20003 | 2.869e-08 | 0.39111 | 41552.5166 | 0.35809 | 0.89917 | 0.00078938 | 0.93631 | 2.4094e-06 | 0.75545 | 50430.3175 | 0.1881 | 0.88842 | 0.077524 |  | 0.08616
0.92116 | 1.593e-06 | 0.11773 | 13804.0619 | 0.98479 | 0.95894 | 0.016272 |  | 0.93757 | 2.0884e-07 | 0.42288 | 42238.7473 | 0.22726 | 0.88034 | 0.0060719 | 0.86713 | 2.0277e-06 | 0.11355 | 34490.2042 | 0.9188 | 0.9732 | 0.038792 |  | 0.061136
0.7079 | 9.4245e-07 | 0.93095 | 23543.0707 | 0.054782 | 0.76687 | 0.027755 |  | 0.64649 | 9.2984e-08 | 0.80152 | 52021.3518 | 0.058061 | 0.83396 | 0.0033694 | 0.098571 | 5.6605e-07 | 0.51493 | 44244.4645 | 0.37607 | 0.91666 | 0.015611 |  | 0.046735
0.84661 | 1.2722e-06 | 0.56983 | 18127.5759 | 0.11459 | 0.79571 | 0.031943 |  | 0.2187 | 3.0893e-08 | 0.7022 | 48832.4385 | 0.48763 | 0.91396 | 0.00092223 | 0.56623 | 1.3041e-06 | 0.92644 | 58686.2891 | 0.47084 | 0.92723 | 0.043796 |  | 0.076661
0.21791 | 3.3246e-07 | 0.04161 | 12376.3279 | 0.89217 | 0.92923 | 0.0039729 |  | 0.74475 | 1.1582e-07 | 0.65498 | 47560.5348 | 0.84195 | 0.95103 | 0.003116 | 0.97697 | 2.8976e-06 | 0.61789 | 46629.5732 | 0.8215 | 0.96158 | 0.074715 |  | 0.081803
0.31074 | 4.2874e-07 | 0.015161 | 11348.3534 | 0.41491 | 0.85928 | 0.0073754 |  | 0.81429 | 1.3747e-07 | 0.93164 | 59137.6563 | 0.87249 | 0.95493 | 0.0044243 | 0.59485 | 1.3528e-06 | 0.40883 | 41935.6161 | 0.8198 | 0.9614 | 0.031845 |  | 0.043645
0.61786 | 7.9536e-07 | 0.98277 | 26713.721 | 0.23857 | 0.82887 | 0.020729 |  | 0.23429 | 3.2738e-08 | 0.82707 | 53025.7447 | 0.44887 | 0.90977 | 0.0010484 | 0.38435 | 1.0245e-06 | 0.048133 | 31487.7672 | 0.0058716 | 0.78236 | 0.032152 |  | 0.053929
0.57089 | 7.2922e-07 | 0.6345 | 18746.3928 | 0.37997 | 0.85396 | 0.015166 |  | 0.98867 | 3.1606e-07 | 0.24458 | 38241.2691 | 0.61334 | 0.92683 | 0.0076269 | 0.98814 | 3.2001e-06 | 0.29524 | 39433.5931 | 0.58726 | 0.93887 | 0.076376 |  | 0.099168
0.16198 | 2.731e-07 | 0.24069 | 15201.9752 | 0.65336 | 0.89216 | 0.004432 |  | 0.9462 | 2.1835e-07 | 0.8937 | 56347.2487 | 0.10999 | 0.85435 | 0.0080417 | 0.90228 | 2.1911e-06 | 0.86565 | 54787.3531 | 0.24348 | 0.89837 | 0.073428 |  | 0.085902
0.88424 | 1.4097e-06 | 0.048805 | 12565.2516 | 0.7623 | 0.90734 | 0.019479 |  | 0.12502 | 1.9761e-08 | 0.36438 | 40972.0371 | 0.54414 | 0.91984 | 0.00051113 | 0.6173 | 1.3925e-06 | 0.070113 | 32696.0774 | 0.4668 | 0.92681 | 0.030026 |  | 0.050016
0.31174 | 4.2977e-07 | 0.59774 | 18388.8302 | 0.11811 | 0.79697 | 0.010793 |  | 0.97169 | 2.5898e-07 | 0.73494 | 49789.744 | 0.0064713 | 0.77374 | 0.010122 | 0.8238 | 1.8714e-06 | 0.46812 | 43217.5552 | 0.81741 | 0.96115 | 0.045236 |  | 0.066151
0.6145 | 7.9043e-07 | 0.17558 | 14523.5696 | 0.55944 | 0.87956 | 0.013388 |  | 0.89052 | 1.7249e-07 | 0.81123 | 52391.028 | 0.4754 | 0.91265 | 0.0054437 | 0.088963 | 5.4515e-07 | 0.48841 | 43660.0666 | 0.17786 | 0.88633 | 0.015976 |  | 0.034808
0.29546 | 4.1285e-07 | 0.25051 | 15297.128 | 0.35815 | 0.85051 | 0.0080919 |  | 0.55081 | 7.5562e-08 | 0.90916 | 57360.8948 | 0.18155 | 0.87188 | 0.0027376 | 0.11039 | 5.9049e-07 | 0.1214 | 34766.0146 | 0.99008 | 0.98832 | 0.010749 |  | 0.021578
0.14732 | 2.5702e-07 | 0.20111 | 14801.3059 | 0.025871 | 0.74053 | 0.0072506 |  | 0.019645 | 5.21e-09 | 0.60163 | 46236.0941 | 0.24703 | 0.88361 | 0.00015955 | 0.014641 | 3.0114e-07 | 0.34784 | 40609.9758 | 0.75574 | 0.95493 | 0.0070279 |  | 0.014438
0.41711 | 5.4262e-07 | 0.72344 | 19704.8488 | 0.019409 | 0.73105 | 0.016692 |  | 0.41121 | 5.4847e-08 | 0.33078 | 40233.3029 | 0.91281 | 0.96079 | 0.0012485 | 0.92881 | 2.3535e-06 | 0.46876 | 43231.3357 | 0.099685 | 0.86584 | 0.071705 |  | 0.089646
0.64409 | 8.3505e-07 | 0.9227 | 23264.7738 | 0.34699 | 0.8487 | 0.019311 |  | 0.010773 | 3.4481e-09 | 0.277 | 39012.8292 | 0.87833 | 0.95572 | 7.7657e-05 | 0.45927 | 1.1354e-06 | 0.80771 | 52255.1908 | 0.8383 | 0.96338 | 0.032221 |  | 0.05161
0.60936 | 7.8295e-07 | 0.59458 | 18358.8487 | 0.84402 | 0.92022 | 0.012086 |  | 0.47239 | 6.3415e-08 | 0.40112 | 41769.0665 | 0.57709 | 0.92319 | 0.0016494 | 0.5112 | 1.2152e-06 | 0.83327 | 53286.3641 | 0.36516 | 0.91534 | 0.038647 |  | 0.052382
0.9004 | 1.482e-06 | 0.81307 | 20907.3351 | 0.43241 | 0.86186 | 0.031286 |  | 0.67923 | 9.9883e-08 | 0.32993 | 40214.3084 | 0.83616 | 0.95033 | 0.0023432 | 0.98108 | 2.9883e-06 | 0.41803 | 42134.025 | 0.8922 | 0.96965 | 0.068989 |  | 0.10262
0.18627 | 2.9918e-07 | 0.57877 | 18210.4467 | 0.31962 | 0.84412 | 0.0063849 |  | 0.079296 | 1.4033e-08 | 0.34437 | 40533.7196 | 0.20047 | 0.87556 | 0.000402 | 0.58818 | 1.3413e-06 | 0.60164 | 46236.2625 | 0.5485 | 0.9351 | 0.036621 |  | 0.043408
0.84066 | 1.2534e-06 | 0.34806 | 16185.7585 | 0.23544 | 0.82822 | 0.027262 |  | 0.85231 | 1.5277e-07 | 0.80926 | 52314.6563 | 0.088515 | 0.84721 | 0.0054303 | 0.87641 | 2.0668e-06 | 0.0061155 | 26606.6862 | 0.31351 | 0.90872 | 0.041512 |  | 0.074204
0.49134 | 6.2818e-07 | 0.18457 | 14623.4927 | 0.8746 | 0.92575 | 0.0083379 |  | 0.38822 | 5.1785e-08 | 0.13119 | 35096.0427 | 0.66467 | 0.93197 | 0.0011555 | 0.26805 | 8.5408e-07 | 0.90628 | 57161.7475 | 0.79373 | 0.95871 | 0.026492 |  | 0.035985
0.28293 | 3.9985e-07 | 0.429 | 16885.5488 | 0.64733 | 0.89134 | 0.006815 |  | 0.1472 | 2.2434e-08 | 0.2375 | 38067.8225 | 0.81489 | 0.94783 | 0.00050725 | 0.73673 | 1.6349e-06 | 0.066924 | 32538.5511 | 0.60168 | 0.94025 | 0.033566 |  | 0.040888
0.42213 | 5.4821e-07 | 0.91414 | 23002.1082 | 0.76635 | 0.90794 | 0.010146 |  | 0.44661 | 5.9723e-08 | 0.50089 | 43934.0777 | 0.12424 | 0.85846 | 0.0018667 | 0.14705 | 6.5981e-07 | 0.84984 | 54022.2575 | 0.38148 | 0.9173 | 0.021128 |  | 0.033141
0.46007 | 5.9131e-07 | 0.056573 | 12748.3512 | 0.62023 | 0.8877 | 0.0091626 |  | 0.53062 | 7.2285e-08 | 0.60344 | 46279.443 | 0.74621 | 0.94031 | 0.0019508 | 0.83736 | 1.9164e-06 | 0.83451 | 53339.2859 | 0.79163 | 0.9585 | 0.055956 |  | 0.06707
0.54791 | 6.9879e-07 | 0.79029 | 20567.8059 | 0.62611 | 0.88849 | 0.013211 |  | 0.95971 | 2.3673e-07 | 0.28887 | 39287.5206 | 0.16701 | 0.86884 | 0.0067604 | 0.52713 | 1.2404e-06 | 0.89275 | 56289.1962 | 0.44885 | 0.9249 | 0.040449 |  | 0.06042
0.29583 | 4.1323e-07 | 0.14219 | 14127.6628 | 0.44939 | 0.86433 | 0.0074342 |  | 0.81997 | 1.3956e-07 | 0.53845 | 44770.4445 | 0.38379 | 0.90231 | 0.0040131 | 0.69505 | 1.5428e-06 | 0.02617 | 29790.2312 | 0.64518 | 0.94438 | 0.029219 |  | 0.040666
0.32166 | 4.4013e-07 | 0.005793 | 10562.8473 | 0.4065 | 0.85802 | 0.0074684 |  | 0.57002 | 7.8793e-08 | 0.20841 | 37332.0631 | 0.17912 | 0.87138 | 0.0021693 | 0.14692 | 6.5958e-07 | 0.34919 | 40639.5996 | 0.21689 | 0.89384 | 0.018114 |  | 0.027751
0.17749 | 2.8982e-07 | 0.10734 | 13654.6569 | 0.57599 | 0.88178 | 0.0047461 |  | 0.78434 | 1.2735e-07 | 0.0948 | 33780.7956 | 0.38033 | 0.90189 | 0.0030345 | 0.40683 | 1.0574e-06 | 0.51069 | 44150.4472 | 0.50353 | 0.93061 | 0.028151 |  | 0.035931
0.80326 | 1.1477e-06 | 0.16672 | 14422.7409 | 0.071758 | 0.77702 | 0.02885 |  | 0.19058 | 2.7575e-08 | 0.085033 | 33376.3194 | 0.90566 | 0.95967 | 0.00053905 | 0.19346 | 7.3856e-07 | 0.26251 | 38672.109 | 0.64005 | 0.9439 | 0.017109 |  | 0.046498
0.50443 | 6.4404e-07 | 0.24459 | 15239.967 | 0.52765 | 0.87525 | 0.011333 |  | 0.74339 | 1.1545e-07 | 0.40477 | 41847.7838 | 0.17938 | 0.87144 | 0.0034053 | 0.54803 | 1.2741e-06 | 0.95624 | 61803.8355 | 0.71326 | 0.95084 | 0.042923 |  | 0.057662
0.42511 | 5.5153e-07 | 0.87877 | 22109.7186 | 0.31938 | 0.84408 | 0.01268 |  | 0.18431 | 2.6835e-08 | 0.49992 | 43912.7166 | 0.29574 | 0.89092 | 0.00078136 | 0.12716 | 6.2324e-07 | 0.3803 | 41318.2735 | 0.22097 | 0.89456 | 0.017274 |  | 0.030735
0.50437 | 6.4396e-07 | 0.87081 | 21939.4509 | 0.98649 | 0.96016 | 0.0090302 |  | 0.0021497 | 1.1588e-09 | 0.8087 | 52293.17 | 0.095304 | 0.84961 | 4.1007e-05 | 0.44882 | 1.1197e-06 | 0.12268 | 34810.1884 | 0.75565 | 0.95492 | 0.023031 |  | 0.032102
0.12193 | 2.2834e-07 | 0.5724 | 18151.2553 | 0.47317 | 0.86771 | 0.0044443 |  | 0.94601 | 2.1813e-07 | 0.78139 | 51296.5996 | 0.38451 | 0.90239 | 0.0069136 | 0.33827 | 9.5736e-07 | 0.32271 | 40053.6702 | 0.4612 | 0.92622 | 0.023946 |  | 0.035304
0.27917 | 3.9596e-07 | 0.21625 | 14958.2204 | 0.46162 | 0.86607 | 0.0072101 |  | 0.17766 | 2.605e-08 | 0.6807 | 48239.3079 | 0.71321 | 0.93689 | 0.00073269 | 0.65057 | 1.454e-06 | 0.75 | 50256.4948 | 0.32055 | 0.90966 | 0.044742 |  | 0.052685
0.44786 | 5.7725e-07 | 0.63856 | 18787.0543 | 0.49547 | 0.87083 | 0.011254 |  | 0.41685 | 5.561e-08 | 0.53777 | 44755.2723 | 0.95873 | 0.96958 | 0.0013548 | 0.92942 | 2.3578e-06 | 0.2248 | 37751.5926 | 0.62138 | 0.94213 | 0.053883 |  | 0.066492
0.28572 | 4.0275e-07 | 0.84283 | 21401.8427 | 0.13619 | 0.80303 | 0.01041 |  | 0.30557 | 4.1311e-08 | 0.32138 | 40023.8409 | 0.70453 | 0.936 | 0.0010054 | 0.1756 | 7.0913e-07 | 0.75456 | 50401.7452 | 0.24264 | 0.89823 | 0.022374 |  | 0.03379
0.3384 | 4.577e-07 | 0.48062 | 17331.4689 | 0.44438 | 0.8636 | 0.0088941 |  | 0.85522 | 1.5409e-07 | 0.46299 | 43106.1047 | 0.0022048 | 0.74772 | 0.0058886 | 0.43653 | 1.1013e-06 | 0.38718 | 41467.4008 | 0.62762 | 0.94272 | 0.027053 |  | 0.041835
0.4536 | 5.8385e-07 | 0.8192 | 21003.9673 | 0.46365 | 0.86636 | 0.012147 |  | 0.54389 | 7.4426e-08 | 0.56641 | 45408.2448 | 0.11534 | 0.85595 | 0.0023855 | 0.52618 | 1.2389e-06 | 0.30336 | 39618.3756 | 0.59892 | 0.93998 | 0.029581 |  | 0.044114
0.39148 | 5.1446e-07 | 0.13705 | 14062.5265 | 0.10225 | 0.79102 | 0.012279 |  | 0.41984 | 5.6017e-08 | 0.3399 | 40434.9878 | 0.13624 | 0.86164 | 0.0016548 | 0.59602 | 1.3548e-06 | 0.09533 | 33801.9591 | 0.79083 | 0.95842 | 0.026881 |  | 0.040816
0.71806 | 9.6131e-07 | 0.34724 | 16178.5963 | 0.86293 | 0.92357 | 0.013618 |  | 0.011815 | 3.6727e-09 | 0.81855 | 52678.7784 | 0.003328 | 0.75746 | 0.00015131 | 0.26589 | 8.5085e-07 | 0.68759 | 48426.5546 | 0.55474 | 0.93571 | 0.024069 |  | 0.037838
0.81364 | 1.1751e-06 | 0.79265 | 20601.6734 | 0.73496 | 0.9034 | 0.020879 |  | 0.47475 | 6.376e-08 | 0.83143 | 53208.0413 | 0.42719 | 0.90735 | 0.0020566 | 0.73605 | 1.6333e-06 | 0.19916 | 37089.034 | 0.94727 | 0.97765 | 0.032809 |  | 0.055745
0.53362 | 6.8042e-07 | 0.081854 | 13246.0903 | 0.8889 | 0.92856 | 0.0084426 |  | 0.0085289 | 2.9404e-09 | 0.21604 | 37529.2412 | 0.28679 | 0.88964 | 7.7513e-05 | 0.24858 | 8.2476e-07 | 0.44391 | 42692.7758 | 0.78615 | 0.95794 | 0.019904 |  | 0.028424
0.12767 | 2.3494e-07 | 0.14374 | 14147.1872 | 0.32286 | 0.84467 | 0.0046005 |  | 0.7634 | 1.2103e-07 | 0.61183 | 46481.7875 | 0.061341 | 0.83565 | 0.004093 | 0.68746 | 1.5271e-06 | 0.43756 | 42555.7307 | 0.090213 | 0.86248 | 0.04642 |  | 0.055113
0.62469 | 8.0549e-07 | 0.78951 | 20556.79 | 0.19259 | 0.81856 | 0.019579 |  | 0.19522 | 2.8123e-08 | 0.97261 | 64481.1036 | 0.19613 | 0.87474 | 0.0011017 | 0.48878 | 1.1803e-06 | 0.70833 | 49006.2782 | 0.52659 | 0.93293 | 0.033916 |  | 0.054597
0.47682 | 6.1089e-07 | 0.40014 | 16637.3238 | 0.7049 | 0.89918 | 0.0099645 |  | 0.65652 | 9.5035e-08 | 0.39695 | 41678.8533 | 0.83568 | 0.95027 | 0.002296 | 0.74053 | 1.6438e-06 | 0.81 | 52343.2969 | 0.018514 | 0.81383 | 0.06182 |  | 0.074081
0.25318 | 3.6907e-07 | 0.15089 | 14235.1788 | 0.36864 | 0.85219 | 0.0070176 |  | 0.84052 | 1.4766e-07 | 0.68851 | 48451.8544 | 0.74191 | 0.93986 | 0.0041401 | 0.2602 | 8.423e-07 | 0.44929 | 42809.1471 | 0.65297 | 0.94512 | 0.021089 |  | 0.032247
0.38692 | 5.095e-07 | 0.53274 | 17790.7253 | 0.46069 | 0.86594 | 0.0099079 |  | 0.75494 | 1.1862e-07 | 0.94214 | 60150.4075 | 0.59008 | 0.9245 | 0.0040827 | 0.3368 | 9.5522e-07 | 0.59068 | 45975.2039 | 0.18399 | 0.88759 | 0.028896 |  | 0.042886
0.74568 | 1.0156e-06 | 0.55595 | 18000.2864 | 0.7672 | 0.90806 | 0.01648 |  | 0.093759 | 1.5891e-08 | 0.052462 | 31752.0517 | 0.21565 | 0.87832 | 0.00039097 | 0.84375 | 1.9388e-06 | 0.4335 | 42468.002 | 0.040105 | 0.83663 | 0.062188 |  | 0.079059
0.023815 | 8.9769e-08 | 0.59037 | 18319.0637 | 0.32471 | 0.84499 | 0.0019138 |  | 0.84167 | 1.4814e-07 | 0.78357 | 51372.618 | 0.22071 | 0.87921 | 0.0049132 | 0.12136 | 6.1213e-07 | 0.82198 | 52817.1265 | 0.08135 | 0.85905 | 0.021445 |  | 0.028272
0.28576 | 4.0279e-07 | 0.85434 | 21612.8743 | 0.077067 | 0.77977 | 0.011165 |  | 0.23767 | 3.3139e-08 | 0.085508 | 33396.6472 | 0.75005 | 0.94071 | 0.00069266 | 0.49735 | 1.1936e-06 | 0.92323 | 58421.2189 | 0.55921 | 0.93615 | 0.039314 |  | 0.051172
0.4454 | 5.7445e-07 | 0.71456 | 19601.2428 | 0.88753 | 0.92828 | 0.0088351 |  | 0.76997 | 1.2296e-07 | 0.40914 | 41942.2904 | 0.90854 | 0.96011 | 0.0029053 | 0.08241 | 5.3027e-07 | 0.2968 | 39469.1016 | 0.18977 | 0.88875 | 0.014468 |  | 0.026208
0.97909 | 2.2001e-06 | 0.5277 | 17745.6805 | 0.78934 | 0.91138 | 0.034871 |  | 0.37308 | 4.9807e-08 | 0.96942 | 63860.3278 | 0.49356 | 0.91459 | 0.0018272 | 0.15237 | 6.6926e-07 | 0.93826 | 59758.4419 | 0.16528 | 0.88362 | 0.024493 |  | 0.06119
0.98167 | 2.2588e-06 | 0.74464 | 19961.1308 | 0.92148 | 0.93577 | 0.033805 |  | 0.092515 | 1.5733e-08 | 0.46808 | 43216.5973 | 0.92667 | 0.9631 | 0.00037828 | 0.96458 | 2.6953e-06 | 0.14593 | 35567.5127 | 0.0043986 | 0.77481 | 0.090308 |  | 0.12449
0.8403 | 1.2523e-06 | 0.32701 | 16000.3489 | 0.045234 | 0.7599 | 0.033951 |  | 0.87775 | 1.6526e-07 | 0.75214 | 50324.4369 | 0.75734 | 0.94148 | 0.0047621 | 0.71613 | 1.5881e-06 | 0.4353 | 42506.8924 | 0.81022 | 0.9604 | 0.037926 |  | 0.076639
0.76348 | 1.0534e-06 | 0.29571 | 15719.3226 | 0.94751 | 0.94286 | 0.013079 |  | 0.71065 | 1.0712e-07 | 0.21817 | 37583.5241 | 0.81049 | 0.94732 | 0.0024013 | 0.086196 | 5.3893e-07 | 0.1236 | 34841.4584 | 0.44198 | 0.92415 | 0.012257 |  | 0.027738
0.47406 | 6.0764e-07 | 0.14804 | 14200.3312 | 0.8618 | 0.92336 | 0.008063 |  | 0.49527 | 6.6807e-08 | 0.78319 | 51359.5306 | 0.53226 | 0.91862 | 0.0020522 | 0.3409 | 9.612e-07 | 0.33878 | 40410.4448 | 0.69902 | 0.94948 | 0.022694 |  | 0.032809
0.31568 | 4.3388e-07 | 0.76639 | 20239.7754 | 0.71566 | 0.90068 | 0.0077297 |  | 0.14652 | 2.2352e-08 | 0.34045 | 40447.318 | 0.65369 | 0.93087 | 0.00055615 | 0.053008 | 4.5454e-07 | 0.42073 | 42192.356 | 0.31674 | 0.90915 | 0.012335 |  | 0.020621
0.17334 | 2.8537e-07 | 0.60768 | 18483.9206 | 0.24861 | 0.83093 | 0.0064178 |  | 0.024957 | 6.1512e-09 | 0.77412 | 51046.8168 | 0.51033 | 0.91635 | 0.00018894 | 0.37449 | 1.0101e-06 | 0.13819 | 35323.3668 | 0.1538 | 0.88101 | 0.026247 |  | 0.032853
0.64238 | 8.324e-07 | 0.3606 | 16295.2714 | 0.90306 | 0.93153 | 0.01131 |  | 0.67398 | 9.8736e-08 | 0.88923 | 56077.4988 | 0.81305 | 0.94761 | 0.0030765 | 0.81832 | 1.854e-06 | 0.27807 | 39037.8031 | 0.20307 | 0.89132 | 0.049905 |  | 0.064292
0.94434 | 1.7556e-06 | 0.50924 | 17582.0512 | 0.94295 | 0.94149 | 0.023529 |  | 0.4905 | 6.6091e-08 | 0.33489 | 40324.3591 | 0.41546 | 0.90602 | 0.0017514 | 0.2142 | 7.7168e-07 | 0.68189 | 48271.6155 | 0.32923 | 0.91081 | 0.022993 |  | 0.048274
0.16609 | 2.7756e-07 | 0.54909 | 17937.9412 | 0.91207 | 0.93354 | 0.0039398 |  | 0.69242 | 1.0284e-07 | 0.4552 | 42937.2109 | 0.64025 | 0.92952 | 0.0026871 | 0.47737 | 1.1628e-06 | 0.50346 | 43990.701 | 0.64687 | 0.94454 | 0.029807 |  | 0.036434
0.31678 | 4.3503e-07 | 0.52892 | 17756.567 | 0.094002 | 0.78761 | 0.011136 |  | 0.95219 | 2.2587e-07 | 0.78236 | 51330.4384 | 0.64178 | 0.92968 | 0.0067808 | 0.33566 | 9.5356e-07 | 0.13948 | 35364.5219 | 0.29333 | 0.90593 | 0.023133 |  | 0.04105
0.39057 | 5.1346e-07 | 0.14021 | 14102.688 | 0.68756 | 0.8968 | 0.0078889 |  | 0.83193 | 1.4416e-07 | 0.72699 | 49550.4834 | 0.62054 | 0.92755 | 0.0042279 | 0.92745 | 2.3439e-06 | 0.71649 | 49241.4349 | 0.0033833 | 0.76807 | 0.091944 |  | 0.10406
0.50121 | 6.4011e-07 | 0.9782 | 26201.9375 | 0.94037 | 0.94074 | 0.011212 |  | 0.23171 | 3.2432e-08 | 0.81232 | 52433.1213 | 0.091935 | 0.84844 | 0.001152 | 0.6388 | 1.4318e-06 | 0.25839 | 38573.9922 | 0.68763 | 0.9484 | 0.032663 |  | 0.045027
0.54428 | 6.9408e-07 | 0.35235 | 16223.3094 | 0.062225 | 0.77161 | 0.018231 |  | 0.71436 | 1.0802e-07 | 0.26532 | 38738.6086 | 0.071118 | 0.84024 | 0.0032697 | 0.62355 | 1.4038e-06 | 0.70794 | 48995.0955 | 0.17586 | 0.88591 | 0.044495 |  | 0.065995
0.41092 | 5.3576e-07 | 0.23714 | 15167.2457 | 0.76877 | 0.9083 | 0.0079943 |  | 0.14558 | 2.2239e-08 | 0.69642 | 48670.4891 | 0.45842 | 0.91082 | 0.00066668 | 0.037192 | 4.039e-07 | 0.54875 | 45003.7917 | 0.47618 | 0.92779 | 0.010987 |  | 0.019648
0.085176 | 1.839e-07 | 0.060911 | 12843.139 | 0.30024 | 0.84072 | 0.0035586 |  | 0.79534 | 1.3091e-07 | 0.74617 | 50136.0792 | 0.25857 | 0.88542 | 0.0042195 | 0.67376 | 1.4993e-06 | 0.038502 | 30832.7315 | 0.9666 | 0.98142 | 0.025124 |  | 0.032902
0.19143 | 3.0465e-07 | 0.36207 | 16308.0671 | 0.41632 | 0.85949 | 0.0058849 |  | 0.48765 | 6.5664e-08 | 0.61117 | 46465.9327 | 0.55855 | 0.92131 | 0.0018582 | 0.50844 | 1.2108e-06 | 0.98472 | 67679.2453 | 0.95108 | 0.97833 | 0.042385 |  | 0.050128
0.92812 | 1.6364e-06 | 0.88926 | 22348.6771 | 0.93665 | 0.9397 | 0.025828 |  | 0.77231 | 1.2366e-07 | 0.64116 | 47207.5963 | 0.11729 | 0.85651 | 0.0040543 | 0.39693 | 1.0429e-06 | 0.38554 | 41431.928 | 0.67539 | 0.94724 | 0.025285 |  | 0.055167
0.20499 | 3.1894e-07 | 0.75091 | 20039.7266 | 0.72492 | 0.90198 | 0.0056211 |  | 0.23034 | 3.227e-08 | 0.32232 | 40044.7995 | 0.79884 | 0.946 | 0.00076389 | 0.80296 | 1.8074e-06 | 0.89413 | 56373.8511 | 0.36515 | 0.91534 | 0.060037 |  | 0.066422
0.51845 | 6.6132e-07 | 0.8312 | 21200.5529 | 0.67928 | 0.89567 | 0.012323 |  | 0.57695 | 7.9986e-08 | 0.89966 | 56722.0419 | 0.35961 | 0.89936 | 0.0027454 | 0.14019 | 6.4744e-07 | 0.068175 | 32600.8995 | 0.36109 | 0.91484 | 0.014485 |  | 0.029553
0.47271 | 6.0605e-07 | 0.33176 | 16042.376 | 0.42409 | 0.86064 | 0.011582 |  | 0.42155 | 5.625e-08 | 0.48094 | 43496.7495 | 0.74934 | 0.94064 | 0.0014432 | 0.12663 | 6.2224e-07 | 0.20855 | 37335.6815 | 0.098959 | 0.8656 | 0.017381 |  | 0.030406
0.74621 | 1.0167e-06 | 0.44682 | 17038.9786 | 0.73744 | 0.90375 | 0.016401 |  | 0.31514 | 4.2488e-08 | 0.45451 | 42922.2717 | 0.07389 | 0.84144 | 0.0013574 | 0.79634 | 1.7882e-06 | 0.033132 | 30414.4669 | 0.8295 | 0.96243 | 0.032058 |  | 0.049817
0.3503 | 4.7027e-07 | 0.45357 | 17097.1749 | 0.19128 | 0.81825 | 0.010777 |  | 0.10769 | 1.7635e-08 | 0.36976 | 41089.2072 | 0.47774 | 0.9129 | 0.00046531 | 0.094279 | 5.5684e-07 | 0.32962 | 40207.3445 | 0.33273 | 0.91126 | 0.01453 |  | 0.025772
0.72536 | 9.7522e-07 | 0.33195 | 16044.0587 | 0.56592 | 0.88043 | 0.017103 |  | 0.47104 | 6.3219e-08 | 0.3778 | 41263.9673 | 0.11449 | 0.8557 | 0.0019153 | 0.30145 | 9.0353e-07 | 0.89635 | 56511.7423 | 0.73611 | 0.95303 | 0.028049 |  | 0.047067
0.49782 | 6.36e-07 | 0.49512 | 17457.9778 | 0.69965 | 0.89846 | 0.010645 |  | 0.92059 | 1.9336e-07 | 0.33776 | 40387.8375 | 0.60314 | 0.92581 | 0.0048717 | 0.031183 | 3.8144e-07 | 0.89064 | 56161.4137 | 0.92906 | 0.9747 | 0.011285 |  | 0.026802
0.30679 | 4.2462e-07 | 0.52988 | 17765.1614 | 0.93518 | 0.93929 | 0.0058009 |  | 0.59725 | 8.3582e-08 | 0.94895 | 60897.9396 | 0.087423 | 0.84681 | 0.0032767 | 0.21431 | 7.7186e-07 | 0.3303 | 40222.5079 | 0.036207 | 0.83353 | 0.024195 |  | 0.033272
0.58073 | 7.4261e-07 | 0.61345 | 18539.5736 | 0.030901 | 0.74655 | 0.021627 |  | 0.8397 | 1.4732e-07 | 0.73764 | 49872.2347 | 0.89738 | 0.95842 | 0.0040575 | 0.81406 | 1.8407e-06 | 0.52271 | 44417.6728 | 0.2901 | 0.90547 | 0.052259 |  | 0.077944
0.89206 | 1.4435e-06 | 0.52682 | 17737.8089 | 0.10408 | 0.79174 | 0.03647 |  | 0.61074 | 8.6055e-08 | 0.87592 | 55324.3175 | 0.16362 | 0.8681 | 0.0030608 | 0.14211 | 6.5093e-07 | 0.11326 | 34479.7386 | 0.44818 | 0.92482 | 0.014665 |  | 0.054196
0.50804 | 6.4845e-07 | 0.4274 | 16871.8574 | 0.10915 | 0.79369 | 0.016061 |  | 0.71816 | 1.0895e-07 | 0.70713 | 48971.9766 | 0.27084 | 0.88729 | 0.0034428 | 0.65273 | 1.4581e-06 | 0.77098 | 50940.5176 | 0.89519 | 0.97003 | 0.039855 |  | 0.059359
0.72467 | 9.7389e-07 | 0.92154 | 23227.8036 | 0.31591 | 0.84348 | 0.022894 |  | 0.5024 | 6.7888e-08 | 0.58108 | 45749.186 | 0.088328 | 0.84714 | 0.0022246 | 0.2004 | 7.4975e-07 | 0.074149 | 32888.7673 | 0.11133 | 0.86961 | 0.019285 |  | 0.044404
0.30024 | 4.1781e-07 | 0.61584 | 18562.7819 | 0.50134 | 0.87164 | 0.008078 |  | 0.30645 | 4.1419e-08 | 0.1459 | 35566.6944 | 0.39037 | 0.90309 | 0.0010168 | 0.1845 | 7.2391e-07 | 0.48063 | 43490.062 | 0.24819 | 0.89913 | 0.02055 |  | 0.029645
0.086958 | 1.8616e-07 | 0.60844 | 18491.1815 | 0.93254 | 0.93858 | 0.0026171 |  | 0.36491 | 4.8753e-08 | 0.7354 | 49803.7659 | 0.0020371 | 0.74588 | 0.0019908 | 0.92028 | 2.2961e-06 | 0.088041 | 33503.8854 | 0.82467 | 0.96191 | 0.044659 |  | 0.049267
0.19829 | 3.1189e-07 | 0.76699 | 20247.6191 | 0.92924 | 0.93772 | 0.0046625 |  | 0.13923 | 2.1478e-08 | 0.33153 | 40249.8177 | 0.057011 | 0.83341 | 0.00067368 | 0.51536 | 1.2217e-06 | 0.36879 | 41068.0478 | 0.36184 | 0.91493 | 0.032057 |  | 0.037393
0.69243 | 9.1477e-07 | 0.73803 | 19879.7935 | 0.80745 | 0.9142 | 0.015188 |  | 0.01081 | 3.4562e-09 | 0.47768 | 43425.6018 | 0.58647 | 0.92413 | 9.2319e-05 | 0.43195 | 1.0945e-06 | 0.4066 | 41887.3258 | 0.42422 | 0.9222 | 0.028599 |  | 0.043879
0.043252 | 1.2464e-07 | 0.5864 | 18281.7767 | 0.6003 | 0.88504 | 0.0022635 |  | 0.040883 | 8.6996e-09 | 0.087741 | 33491.2885 | 0.50055 | 0.91533 | 0.00019787 | 0.41872 | 1.0749e-06 | 0.34958 | 40648.16 | 0.61439 | 0.94146 | 0.02608 |  | 0.028542
0.60164 | 7.7186e-07 | 0.49538 | 17460.3088 | 0.41803 | 0.85975 | 0.015277 |  | 0.59569 | 8.3299e-08 | 0.15199 | 35753.8059 | 0.41176 | 0.90559 | 0.0020374 | 0.77101 | 1.7193e-06 | 0.21548 | 37514.8538 | 0.58717 | 0.93886 | 0.039486 |  | 0.0568
0.085522 | 1.8434e-07 | 0.52284 | 17702.4056 | 0.94254 | 0.94137 | 0.0024827 |  | 0.87034 | 1.6139e-07 | 0.51726 | 44296.3229 | 0.8055 | 0.94675 | 0.0041369 | 0.35606 | 9.8327e-07 | 0.49948 | 43902.9649 | 0.77247 | 0.95658 | 0.024387 |  | 0.031007
0.81563 | 1.1805e-06 | 0.066316 | 12955.021 | 0.87606 | 0.92603 | 0.01473 |  | 0.63936 | 9.1556e-08 | 0.41093 | 41980.8819 | 0.037984 | 0.82131 | 0.0030115 | 0.83631 | 1.9128e-06 | 0.86762 | 54887.5704 | 0.75208 | 0.95458 | 0.057722 |  | 0.075464
0.61052 | 7.8464e-07 | 0.93658 | 23750.0038 | 0.48747 | 0.86971 | 0.017059 |  | 0.72746 | 1.1128e-07 | 0.34101 | 40459.6062 | 0.55215 | 0.92066 | 0.0028461 | 0.038468 | 4.0839e-07 | 0.3927 | 41586.9967 | 0.57833 | 0.938 | 0.010183 |  | 0.030088
0.33199 | 4.5096e-07 | 0.80006 | 20709.9267 | 0.54425 | 0.8775 | 0.0089367 |  | 0.84429 | 1.4926e-07 | 0.025721 | 29745.8268 | 0.64665 | 0.93016 | 0.0029779 | 0.95505 | 2.5808e-06 | 0.15383 | 35809.4901 | 0.76558 | 0.9559 | 0.05414 |  | 0.066055
0.76955 | 1.0669e-06 | 0.73366 | 19826.668 | 0.29849 | 0.84041 | 0.023803 |  | 0.28502 | 3.8808e-08 | 0.24152 | 38166.5042 | 0.73927 | 0.93958 | 0.00090123 | 0.7776 | 1.7366e-06 | 0.4224 | 42228.3862 | 0.76817 | 0.95615 | 0.041729 |  | 0.066434
0.17366 | 2.8571e-07 | 0.090058 | 13385.4115 | 0.39419 | 0.85616 | 0.0052372 |  | 0.91276 | 1.8728e-07 | 0.89367 | 56345.369 | 0.10022 | 0.85126 | 0.0069315 | 0.45183 | 1.1242e-06 | 0.81871 | 52685.3067 | 0.23499 | 0.89696 | 0.036709 |  | 0.048878
0.59759 | 7.6611e-07 | 0.65461 | 18949.9682 | 0.65173 | 0.89193 | 0.013727 |  | 0.2617 | 3.6001e-08 | 0.15616 | 35879.5888 | 0.9256 | 0.96292 | 0.00073885 | 0.37355 | 1.0087e-06 | 0.28639 | 39230.3768 | 0.57603 | 0.93778 | 0.024053 |  | 0.038519
0.011197 | 5.9996e-08 | 0.53396 | 17801.6197 | 0.42851 | 0.86129 | 0.0011889 |  | 0.91287 | 1.8736e-07 | 0.66638 | 47857.5945 | 0.80806 | 0.94704 | 0.005115 | 0.30306 | 9.059e-07 | 0.22808 | 37834.0579 | 0.3479 | 0.9132 | 0.022537 |  | 0.028841
0.080388 | 1.7773e-07 | 0.20864 | 14879.9973 | 0.95639 | 0.94575 | 0.0020952 |  | 0.14487 | 2.2154e-08 | 0.85165 | 54106.2815 | 0.15131 | 0.86531 | 0.00078 | 0.62874 | 1.4132e-06 | 0.6706 | 47969.2784 | 0.65892 | 0.94568 | 0.038779 |  | 0.041654
0.60231 | 7.7282e-07 | 0.048791 | 12564.8986 | 0.063388 | 0.7723 | 0.019164 |  | 0.3822 | 5.0995e-08 | 0.22618 | 37786.4329 | 0.084526 | 0.84572 | 0.001504 | 0.86581 | 2.0223e-06 | 0.29688 | 39471.0562 | 0.22601 | 0.89544 | 0.054262 |  | 0.074931
0.42957 | 5.5653e-07 | 0.9553 | 24580.8835 | 0.5285 | 0.87537 | 0.012064 |  | 0.26791 | 3.6745e-08 | 0.56201 | 45306.7915 | 0.32672 | 0.89514 | 0.0010826 | 0.61388 | 1.3863e-06 | 0.69 | 48492.6631 | 0.89964 | 0.9706 | 0.036196 |  | 0.049342
0.75351 | 1.032e-06 | 0.18096 | 14583.7028 | 0.031253 | 0.74694 | 0.028498 |  | 0.44011 | 5.8813e-08 | 0.61441 | 46544.5775 | 0.59106 | 0.9246 | 0.001654 | 0.49838 | 1.1951e-06 | 0.6672 | 47879.3042 | 0.36724 | 0.91559 | 0.035034 |  | 0.065185
0.76859 | 1.0647e-06 | 0.95176 | 24402.2298 | 0.61985 | 0.88765 | 0.022009 |  | 0.4069 | 5.4267e-08 | 0.37433 | 41188.7285 | 0.87533 | 0.95531 | 0.0012801 | 0.88842 | 2.1213e-06 | 0.69783 | 48709.7714 | 0.88865 | 0.9692 | 0.055797 |  | 0.079086
0.6818 | 8.9641e-07 | 0.38492 | 16506.0355 | 0.53835 | 0.8767 | 0.016168 |  | 0.021168 | 5.4864e-09 | 0.89377 | 56351.731 | 0.22508 | 0.87997 | 0.00019372 | 0.62728 | 1.4105e-06 | 0.65168 | 47475.5981 | 0.16032 | 0.88251 | 0.044067 |  | 0.060428
0.45072 | 5.8054e-07 | 0.25053 | 15297.3172 | 0.58412 | 0.88287 | 0.0098769 |  | 0.86026 | 1.5644e-07 | 0.037674 | 30771.103 | 0.79208 | 0.94525 | 0.0030255 | 0.67711 | 1.506e-06 | 0.14676 | 35593.2778 | 0.040392 | 0.83685 | 0.043952 |  | 0.056854
0.4075 | 5.3198e-07 | 0.34759 | 16181.6805 | 0.40885 | 0.85838 | 0.010295 |  | 0.79075 | 1.2941e-07 | 0.68513 | 48359.552 | 0.86661 | 0.95415 | 0.0035053 | 0.6498 | 1.4526e-06 | 0.61219 | 46490.703 | 0.78849 | 0.95818 | 0.037674 |  | 0.051474
0.35574 | 4.7605e-07 | 0.039497 | 12316.4381 | 0.18861 | 0.81759 | 0.010004 |  | 0.64555 | 9.2793e-08 | 0.22763 | 37822.6702 | 0.2408 | 0.8826 | 0.0025031 | 0.47526 | 1.1596e-06 | 0.34188 | 40478.7035 | 0.79143 | 0.95848 | 0.026713 |  | 0.03922
0.86888 | 1.3493e-06 | 0.077031 | 13159.9573 | 0.95145 | 0.9441 | 0.014988 |  | 0.97348 | 2.6309e-07 | 0.428 | 42349.2336 | 0.94364 | 0.96627 | 0.0061601 | 0.093755 | 5.557e-07 | 0.20812 | 37324.4753 | 0.66088 | 0.94587 | 0.012444 |  | 0.033593
0.60766 | 7.8049e-07 | 0.55012 | 17947.2681 | 0.86797 | 0.9245 | 0.011637 |  | 0.94669 | 2.1894e-07 | 0.46823 | 43219.9006 | 0.73169 | 0.93879 | 0.0056156 | 0.06173 | 4.789e-07 | 0.040988 | 31012.1445 | 0.87816 | 0.96792 | 0.0085336 |  | 0.025786
0.075211 | 1.7093e-07 | 0.67733 | 19188.1172 | 0.0072052 | 0.70039 | 0.0056348 |  | 0.33711 | 4.5222e-08 | 0.62275 | 46748.8378 | 0.93233 | 0.96411 | 0.0011613 | 0.13671 | 6.4107e-07 | 0.34532 | 40554.486 | 0.76526 | 0.95587 | 0.014904 |  | 0.0217
0.68734 | 9.059e-07 | 0.53882 | 17845.2566 | 0.52459 | 0.87483 | 0.017004 |  | 0.74306 | 1.1536e-07 | 0.36817 | 41054.5333 | 0.72557 | 0.93816 | 0.0028466 | 0.2441 | 8.1795e-07 | 0.6244 | 46789.3188 | 0.75813 | 0.95517 | 0.02149 |  | 0.041341
0.55731 | 7.111e-07 | 0.44942 | 17061.4537 | 0.61691 | 0.88726 | 0.012405 |  | 0.8806 | 1.6681e-07 | 0.45709 | 42978.2144 | 0.26109 | 0.88581 | 0.0048438 | 0.54284 | 1.2657e-06 | 0.3473 | 40598.1227 | 0.067083 | 0.85276 | 0.038233 |  | 0.055482
0.45069 | 5.8049e-07 | 0.67814 | 19196.8532 | 0.71891 | 0.90114 | 0.010048 |  | 0.31078 | 4.1951e-08 | 0.57265 | 45552.7651 | 0.88414 | 0.95652 | 0.0010737 | 0.57748 | 1.323e-06 | 0.79354 | 51728.0912 | 0.97802 | 0.98422 | 0.035508 |  | 0.04663
0.12773 | 2.3501e-07 | 0.58179 | 18238.5576 | 0.62199 | 0.88794 | 0.0042099 |  | 0.69798 | 1.0412e-07 | 0.24184 | 38174.4514 | 0.47992 | 0.91314 | 0.002607 | 0.11387 | 5.9746e-07 | 0.98439 | 67565.2451 | 0.82549 | 0.962 | 0.021406 |  | 0.028223
0.31622 | 4.3445e-07 | 0.55928 | 18030.6422 | 0.96706 | 0.94976 | 0.005632 |  | 0.38652 | 5.1561e-08 | 0.87073 | 55048.2529 | 0.019294 | 0.80225 | 0.0020317 | 0.1907 | 7.3407e-07 | 0.84712 | 53897.1921 | 0.12078 | 0.87243 | 0.025462 |  | 0.033125
0.89622 | 1.4623e-06 | 0.60649 | 18472.4883 | 0.42406 | 0.86064 | 0.029476 |  | 0.86545 | 1.5894e-07 | 0.025734 | 29747.1115 | 0.98078 | 0.97609 | 0.0026404 | 0.56528 | 1.3026e-06 | 0.11743 | 34627.7631 | 0.86294 | 0.96613 | 0.025653 |  | 0.05777
0.83325 | 1.2308e-06 | 0.23003 | 15096.9901 | 0.96967 | 0.95087 | 0.014132 |  | 0.94236 | 2.1395e-07 | 0.10749 | 34269.3738 | 0.95467 | 0.96863 | 0.0041388 | 0.21498 | 7.7292e-07 | 0.040872 | 31003.8937 | 0.51881 | 0.93215 | 0.015763 |  | 0.034033
0.14592 | 2.5547e-07 | 0.48731 | 17389.7524 | 0.7139 | 0.90044 | 0.0042283 |  | 0.97568 | 2.6851e-07 | 0.89436 | 56388.0572 | 0.65025 | 0.93053 | 0.0086787 | 0.11938 | 6.083e-07 | 0.7534 | 50364.6581 | 0.73544 | 0.95296 | 0.017104 |  | 0.030011
0.04838 | 1.3273e-07 | 0.40785 | 16703.677 | 0.80405 | 0.91366 | 0.0020167 |  | 0.7149 | 1.0815e-07 | 0.8814 | 55625.84 | 0.16074 | 0.86746 | 0.003865 | 0.45013 | 1.1216e-06 | 0.043793 | 31205.3917 | 0.040457 | 0.8369 | 0.030671 |  | 0.036553
0.55117 | 7.0303e-07 | 0.11944 | 13827.8753 | 0.52878 | 0.8754 | 0.011928 |  | 0.81255 | 1.3684e-07 | 0.18977 | 36836.7443 | 0.23695 | 0.88197 | 0.0036377 | 0.059932 | 4.7404e-07 | 0.31816 | 39951.8797 | 0.52324 | 0.9326 | 0.01163 |  | 0.027196
0.92617 | 1.6239e-06 | 0.59449 | 18358.0717 | 0.91581 | 0.93441 | 0.023258 |  | 0.84566 | 1.4985e-07 | 0.75557 | 50434.1202 | 0.84347 | 0.95122 | 0.0042346 | 0.27453 | 8.6374e-07 | 0.90637 | 57167.7369 | 0.43499 | 0.92339 | 0.028594 |  | 0.056087
0.83442 | 1.2343e-06 | 0.09532 | 13470.562 | 0.74501 | 0.90483 | 0.017812 |  | 0.91601 | 1.8974e-07 | 0.43053 | 42403.9363 | 0.27442 | 0.88783 | 0.005436 | 0.54001 | 1.2611e-06 | 0.14806 | 35633.4857 | 0.99653 | 0.99203 | 0.02317 |  | 0.046418
0.33305 | 4.5208e-07 | 0.56892 | 18119.1998 | 0.33482 | 0.84669 | 0.009539 |  | 0.48877 | 6.5831e-08 | 0.10204 | 34064.2169 | 0.24321 | 0.88299 | 0.0016648 | 0.80501 | 1.8135e-06 | 0.18333 | 36660.4405 | 0.7799 | 0.95732 | 0.038603 |  | 0.049806
0.0061456 | 4.3829e-08 | 0.70595 | 19502.8918 | 0.14503 | 0.80575 | 0.0010902 |  | 0.28647 | 3.8983e-08 | 0.89199 | 56242.9007 | 0.43483 | 0.90821 | 0.0013091 | 0.94029 | 2.4415e-06 | 0.31575 | 39897.8337 | 0.16478 | 0.88351 | 0.067945 |  | 0.070344
0.58687 | 7.5108e-07 | 0.57565 | 18181.4007 | 0.6903 | 0.89717 | 0.012891 |  | 0.2231 | 3.1414e-08 | 0.276 | 38989.4786 | 0.65002 | 0.9305 | 0.00076109 | 0.72562 | 1.6093e-06 | 0.16051 | 36009.065 | 0.061304 | 0.84988 | 0.04579 |  | 0.059442
0.27948 | 3.9628e-07 | 0.28045 | 15579.2777 | 0.17959 | 0.81533 | 0.0089277 |  | 0.73998 | 1.1454e-07 | 0.941 | 60032.2032 | 0.69326 | 0.93485 | 0.0038676 | 0.94502 | 2.4823e-06 | 0.77334 | 51020.4244 | 0.83501 | 0.96302 | 0.069023 |  | 0.081818
0.49769 | 6.3584e-07 | 0.52511 | 17722.6121 | 0.49743 | 0.8711 | 0.012088 |  | 0.11747 | 1.8841e-08 | 0.095942 | 33826.3301 | 0.62064 | 0.92756 | 0.00041512 | 0.81923 | 1.8568e-06 | 0.45805 | 42998.8345 | 0.021894 | 0.81865 | 0.062179 |  | 0.074682
0.97876 | 2.193e-06 | 0.74205 | 19929.1303 | 0.21074 | 0.82282 | 0.052017 |  | 0.81454 | 1.3756e-07 | 0.34762 | 40605.1166 | 0.74596 | 0.94028 | 0.0033456 | 0.50812 | 1.2103e-06 | 0.4418 | 42647.1792 | 0.11478 | 0.87066 | 0.036184 |  | 0.091546
0.6327 | 8.1754e-07 | 0.79629 | 20654.4932 | 0.11619 | 0.79629 | 0.021312 |  | 0.25308 | 3.4972e-08 | 0.49477 | 43799.5226 | 0.38952 | 0.90299 | 0.00098877 | 0.008659 | 2.5729e-07 | 0.63903 | 47154.0307 | 0.10059 | 0.86615 | 0.008271 |  | 0.030572
0.93825 | 1.7074e-06 | 0.57168 | 18144.6624 | 0.6279 | 0.88873 | 0.030408 |  | 0.40705 | 5.4287e-08 | 0.11558 | 34562.5382 | 0.97809 | 0.97511 | 0.0010332 | 0.65695 | 1.4663e-06 | 0.88524 | 55844.2427 | 0.61153 | 0.94119 | 0.046087 |  | 0.077528
0.11701 | 2.2263e-07 | 0.76081 | 20166.57 | 0.91283 | 0.93372 | 0.0033887 |  | 0.90724 | 1.833e-07 | 0.31611 | 39905.8291 | 0.93912 | 0.96538 | 0.0040866 | 0.93035 | 2.3645e-06 | 0.21514 | 37505.9401 | 0.23319 | 0.89666 | 0.061163 |  | 0.068638
0.46789 | 6.004e-07 | 0.25321 | 15323.0929 | 0.70404 | 0.89907 | 0.0094444 |  | 0.35541 | 4.7537e-08 | 0.52206 | 44403.0315 | 0.17156 | 0.86981 | 0.0014601 | 0.83716 | 1.9157e-06 | 0.22001 | 37630.369 | 0.77122 | 0.95646 | 0.041783 |  | 0.052687
0.043035 | 1.2429e-07 | 0.46697 | 17212.9986 | 0.61171 | 0.88656 | 0.0021834 |  | 0.48921 | 6.5897e-08 | 0.15132 | 35733.405 | 0.057365 | 0.8336 | 0.001942 | 0.54416 | 1.2678e-06 | 0.88685 | 55937.415 | 0.6801 | 0.94769 | 0.039413 |  | 0.043539
0.26289 | 3.7912e-07 | 0.21217 | 14916.3988 | 0.65734 | 0.89269 | 0.0060879 |  | 0.44961 | 6.0146e-08 | 0.47812 | 43435.2897 | 0.6799 | 0.9335 | 0.0015697 | 0.47186 | 1.1544e-06 | 0.76886 | 50869.4691 | 0.71246 | 0.95076 | 0.032896 |  | 0.040554
0.63705 | 8.2418e-07 | 0.038917 | 12299.5762 | 0.20687 | 0.82194 | 0.017022 |  | 0.53344 | 7.2735e-08 | 0.30351 | 39621.6505 | 0.5176 | 0.91711 | 0.0018497 | 0.71762 | 1.5914e-06 | 0.6441 | 47282.1299 | 0.94924 | 0.978 | 0.039862 |  | 0.058733
0.092682 | 1.9336e-07 | 0.10699 | 13649.475 | 0.60967 | 0.88629 | 0.0030955 |  | 0.38814 | 5.1773e-08 | 0.25677 | 38535.346 | 0.17477 | 0.87049 | 0.0014557 | 0.36098 | 9.9043e-07 | 0.82053 | 52758.2485 | 0.77292 | 0.95662 | 0.028757 |  | 0.033308
0.47545 | 6.0927e-07 | 0.62444 | 18646.8757 | 0.64786 | 0.89141 | 0.010859 |  | 0.72546 | 1.1078e-07 | 0.20114 | 37141.4826 | 0.99392 | 0.983 | 0.0021872 | 0.44966 | 1.1209e-06 | 0.47007 | 43260.0006 | 0.24697 | 0.89893 | 0.031719 |  | 0.044765
0.8845 | 1.4109e-06 | 0.76041 | 20161.3835 | 0.038868 | 0.75451 | 0.041071 |  | 0.9714 | 2.5836e-07 | 0.65766 | 47629.8307 | 0.32983 | 0.89555 | 0.0078739 | 0.56379 | 1.3001e-06 | 0.61957 | 46670.7228 | 0.20847 | 0.89232 | 0.039334 |  | 0.088279
0.46043 | 5.9173e-07 | 0.68805 | 19303.9857 | 0.39996 | 0.85704 | 0.012305 |  | 0.15632 | 2.3521e-08 | 0.41539 | 42077.157 | 0.81937 | 0.94834 | 0.00057572 | 0.64235 | 1.4385e-06 | 0.12095 | 34750.3546 | 0.58784 | 0.93892 | 0.031163 |  | 0.044045
0.35778 | 4.7821e-07 | 0.80634 | 20803.9229 | 0.26572 | 0.83432 | 0.011091 |  | 0.39351 | 5.2482e-08 | 0.886 | 55888.2411 | 0.98159 | 0.97641 | 0.0015404 | 0.77297 | 1.7244e-06 | 0.22135 | 37664.3901 | 0.74644 | 0.95403 | 0.037926 |  | 0.050557
0.27087 | 3.8737e-07 | 0.23652 | 15161.1947 | 0.48057 | 0.86875 | 0.0070049 |  | 0.33668 | 4.5168e-08 | 0.6025 | 46256.7946 | 0.27032 | 0.88722 | 0.0013731 | 0.95936 | 2.6295e-06 | 0.53633 | 44722.7784 | 0.84973 | 0.96463 | 0.064865 |  | 0.073243
0.68273 | 8.9799e-07 | 0.63581 | 18759.4645 | 0.49977 | 0.87142 | 0.017454 |  | 0.84343 | 1.4889e-07 | 0.91348 | 57670.4696 | 0.18454 | 0.87248 | 0.0054091 | 0.31017 | 9.1633e-07 | 0.30887 | 39743.0981 | 0.37682 | 0.91675 | 0.023376 |  | 0.046239
0.30488 | 4.2263e-07 | 0.89213 | 22417.3846 | 0.50125 | 0.87163 | 0.0088816 |  | 0.17341 | 2.5548e-08 | 0.7236 | 49449.8523 | 0.0090377 | 0.7822 | 0.00098153 | 0.8661 | 2.0235e-06 | 0.7078 | 48991.1764 | 0.7282 | 0.95227 | 0.055662 |  | 0.065525
0.74461 | 1.0135e-06 | 0.62412 | 18643.6725 | 0.45225 | 0.86474 | 0.020178 |  | 0.81077 | 1.362e-07 | 0.32992 | 40214.0744 | 0.88474 | 0.9566 | 0.0031376 | 0.59745 | 1.3573e-06 | 0.44163 | 42643.6487 | 0.82493 | 0.96194 | 0.032365 |  | 0.05568
0.70924 | 9.449e-07 | 0.29425 | 15705.955 | 0.9972 | 0.97276 | 0.0094732 |  | 0.20776 | 2.9602e-08 | 0.12982 | 35050.6932 | 0.49581 | 0.91483 | 0.00069547 | 0.86675 | 2.0262e-06 | 0.64564 | 47321.2274 | 0.50865 | 0.93113 | 0.056862 |  | 0.067031
0.74497 | 1.0142e-06 | 0.54252 | 17878.544 | 0.58063 | 0.8824 | 0.018448 |  | 0.76005 | 1.2007e-07 | 0.083364 | 33304.29 | 0.11832 | 0.85681 | 0.0032191 | 0.61363 | 1.3859e-06 | 0.21073 | 37392.3063 | 0.30262 | 0.90723 | 0.03477 |  | 0.056437
0.11242 | 2.1725e-07 | 0.49316 | 17440.8361 | 0.49963 | 0.8714 | 0.0040982 |  | 0.54233 | 7.4171e-08 | 0.97353 | 64672.3486 | 0.53471 | 0.91888 | 0.0027309 | 0.67302 | 1.4978e-06 | 0.94996 | 61016.4595 | 0.03103 | 0.82889 | 0.060326 |  | 0.067155
0.13104 | 2.3877e-07 | 0.25532 | 15343.2485 | 0.19506 | 0.81916 | 0.0052831 |  | 0.28197 | 3.8439e-08 | 0.78979 | 51592.9089 | 0.65502 | 0.931 | 0.0011555 | 0.93767 | 2.4201e-06 | 0.21415 | 37480.646 | 0.34877 | 0.91331 | 0.0598 |  | 0.066239
0.32107 | 4.3952e-07 | 0.40001 | 16636.1838 | 0.35425 | 0.84989 | 0.0088869 |  | 0.9509 | 2.2418e-07 | 0.17995 | 36566.4839 | 0.28344 | 0.88915 | 0.0058211 | 0.49653 | 1.1923e-06 | 0.52999 | 44580.4635 | 0.82329 | 0.96177 | 0.029553 |  | 0.044262
0.58069 | 7.4255e-07 | 0.1293 | 13961.4562 | 0.32955 | 0.84581 | 0.014414 |  | 0.1813 | 2.648e-08 | 0.64038 | 47187.8838 | 0.43464 | 0.90819 | 0.00078039 | 0.51775 | 1.2255e-06 | 0.29244 | 39369.4357 | 0.36762 | 0.91564 | 0.031145 |  | 0.046339
0.1784 | 2.9079e-07 | 0.877 | 22071.1488 | 0.39319 | 0.856 | 0.0064149 |  | 0.075778 | 1.3573e-08 | 0.8972 | 56565.1866 | 0.88699 | 0.95692 | 0.00041855 | 0.33504 | 9.5266e-07 | 0.050455 | 31631.4923 | 0.9675 | 0.98162 | 0.016324 |  | 0.023158
0.37495 | 4.9658e-07 | 0.27192 | 15500.0512 | 0.07592 | 0.77919 | 0.012604 |  | 0.9079 | 1.8376e-07 | 0.71579 | 49220.9205 | 0.29816 | 0.89126 | 0.0057811 | 0.82081 | 1.8618e-06 | 0.12632 | 34933.7125 | 0.97801 | 0.98422 | 0.034581 |  | 0.052966
0.59552 | 7.6318e-07 | 0.86896 | 21901.1434 | 0.45216 | 0.86472 | 0.016271 |  | 0.14911 | 2.2662e-08 | 0.77279 | 51001.5406 | 0.088336 | 0.84714 | 0.000793 | 0.84883 | 1.9571e-06 | 0.12567 | 34911.6319 | 0.18348 | 0.88749 | 0.049608 |  | 0.066672
0.44643 | 5.7562e-07 | 0.84379 | 21418.8793 | 0.12445 | 0.79917 | 0.015053 |  | 0.43966 | 5.875e-08 | 0.83056 | 53171.208 | 0.34002 | 0.89688 | 0.0019315 | 0.79332 | 1.7797e-06 | 0.10924 | 34333.5778 | 0.86065 | 0.96587 | 0.03483 |  | 0.051814
0.20747 | 3.2154e-07 | 0.60245 | 18433.776 | 0.042074 | 0.75731 | 0.0090801 |  | 0.84523 | 1.4966e-07 | 0.55558 | 45159.3484 | 0.60473 | 0.92597 | 0.0040997 | 0.60534 | 1.3712e-06 | 0.78928 | 51574.6558 | 0.39657 | 0.91907 | 0.042218 |  | 0.055398
0.58801 | 7.5267e-07 | 0.91853 | 23133.7798 | 0.25576 | 0.83236 | 0.0183 |  | 0.31454 | 4.2414e-08 | 0.084464 | 33351.8739 | 0.25961 | 0.88558 | 0.0010515 | 0.9788 | 2.936e-06 | 0.51238 | 44187.9807 | 0.63488 | 0.94341 | 0.075752 |  | 0.095103
0.46538 | 5.9747e-07 | 0.96903 | 25421.5951 | 0.85521 | 0.92218 | 0.011076 |  | 0.92216 | 1.9465e-07 | 0.95741 | 61962.3641 | 0.65748 | 0.93125 | 0.0067882 | 0.49559 | 1.1908e-06 | 0.3949 | 41634.5058 | 0.15674 | 0.88169 | 0.034198 |  | 0.052063
0.97487 | 2.1178e-06 | 0.32366 | 15970.5348 | 0.51757 | 0.87387 | 0.038177 |  | 0.041891 | 8.8512e-09 | 0.13139 | 35102.6234 | 0.6202 | 0.92752 | 0.00020029 | 0.49842 | 1.1952e-06 | 0.70093 | 48796.5512 | 0.55768 | 0.936 | 0.033996 |  | 0.072373
0.091532 | 1.9192e-07 | 0.15555 | 14291.4026 | 0.47842 | 0.86845 | 0.0034027 |  | 0.19048 | 2.7564e-08 | 0.3095 | 39757.1431 | 0.28965 | 0.89005 | 0.00075317 | 0.15077 | 6.6643e-07 | 0.77916 | 51219.3831 | 0.8896 | 0.96932 | 0.018335 |  | 0.02249
0.55995 | 7.1458e-07 | 0.92278 | 23267.2705 | 0.28208 | 0.83742 | 0.017139 |  | 0.52031 | 7.0654e-08 | 0.65727 | 47619.7357 | 0.2074 | 0.87684 | 0.0022374 | 0.79583 | 1.7868e-06 | 0.73144 | 49683.9711 | 0.88692 | 0.96899 | 0.047865 |  | 0.067241
0.81847 | 1.1883e-06 | 0.48007 | 17326.7367 | 0.2209 | 0.8251 | 0.026701 |  | 0.69081 | 1.0247e-07 | 0.90149 | 56841.2234 | 0.55988 | 0.92145 | 0.0033887 | 0.43215 | 1.0948e-06 | 0.76452 | 50725.4848 | 0.79425 | 0.95876 | 0.030577 |  | 0.060667
0.35792 | 4.7837e-07 | 0.74037 | 19908.4607 | 0.81198 | 0.91492 | 0.0079221 |  | 0.39371 | 5.2509e-08 | 0.70496 | 48910.4027 | 0.80208 | 0.94637 | 0.0014619 | 0.41279 | 1.0662e-06 | 0.58294 | 45792.9746 | 0.85147 | 0.96483 | 0.026838 |  | 0.036222
0.3072 | 4.2505e-07 | 0.9738 | 25795.745 | 0.17548 | 0.81426 | 0.01138 |  | 0.83309 | 1.4463e-07 | 0.59018 | 45963.4449 | 0.33069 | 0.89567 | 0.0042988 | 0.13637 | 6.4044e-07 | 0.71213 | 49115.1009 | 0.77647 | 0.95698 | 0.017465 |  | 0.033143
0.37985 | 5.0186e-07 | 0.1222 | 13865.8725 | 0.16486 | 0.81144 | 0.011113 |  | 0.32901 | 4.4209e-08 | 0.9194 | 58116.8602 | 0.52961 | 0.91835 | 0.001496 | 0.77044 | 1.7178e-06 | 0.12357 | 34840.4186 | 0.78633 | 0.95796 | 0.034992 |  | 0.047601
0.5244 | 6.6876e-07 | 0.448 | 17049.14 | 0.35986 | 0.85079 | 0.013592 |  | 0.13657 | 2.1158e-08 | 0.3162 | 39907.8643 | 0.25505 | 0.88487 | 0.00058697 | 0.74952 | 1.6653e-06 | 0.27567 | 38981.7609 | 0.048941 | 0.84277 | 0.050291 |  | 0.06447
0.25539 | 3.7136e-07 | 0.021404 | 11671.2427 | 0.33222 | 0.84626 | 0.0068355 |  | 0.31127 | 4.2012e-08 | 0.17319 | 36376.2303 | 0.42041 | 0.90658 | 0.0010365 | 0.21389 | 7.712e-07 | 0.83845 | 53509.9067 | 0.87362 | 0.96738 | 0.022164 |  | 0.030036
0.64372 | 8.3447e-07 | 0.58731 | 18290.2803 | 0.47986 | 0.86865 | 0.016231 |  | 0.95244 | 2.2621e-07 | 0.8511 | 54080.7687 | 0.93977 | 0.96551 | 0.0065892 | 0.66626 | 1.4844e-06 | 0.030288 | 30172.4861 | 0.88813 | 0.96914 | 0.025716 |  | 0.048536
0.53817 | 6.8623e-07 | 0.37094 | 16385.0864 | 0.63943 | 0.89028 | 0.011601 |  | 0.50416 | 6.8156e-08 | 0.95545 | 61699.5417 | 0.62587 | 0.92809 | 0.0023807 | 0.57191 | 1.3137e-06 | 0.085987 | 33417.0616 | 0.93461 | 0.97556 | 0.024225 |  | 0.038207
0.1045 | 2.0781e-07 | 0.095846 | 13478.9167 | 0.75883 | 0.90683 | 0.0029661 |  | 0.94165 | 2.1317e-07 | 0.69405 | 48604.6843 | 0.20222 | 0.87589 | 0.0068552 | 0.77632 | 1.7332e-06 | 0.29307 | 39383.9957 | 0.23305 | 0.89664 | 0.046296 |  | 0.056117
0.75256 | 1.03e-06 | 0.66603 | 19068.5429 | 0.18276 | 0.81613 | 0.024604 |  | 0.15239 | 2.3052e-08 | 0.43804 | 42566.056 | 0.4475 | 0.90962 | 0.0006288 | 0.30214 | 9.0455e-07 | 0.78804 | 51530.3329 | 0.24881 | 0.89923 | 0.028942 |  | 0.054175
0.63868 | 8.2668e-07 | 0.47742 | 17303.6295 | 0.76561 | 0.90783 | 0.013168 |  | 0.72168 | 1.0982e-07 | 0.58819 | 45916.4888 | 0.53271 | 0.91867 | 0.0030988 | 0.84588 | 1.9464e-06 | 0.817 | 52617.0768 | 0.37169 | 0.91613 | 0.061211 |  | 0.077478
0.36103 | 4.8168e-07 | 0.39215 | 16568.4676 | 0.41684 | 0.85957 | 0.0093554 |  | 0.48249 | 6.4899e-08 | 0.57289 | 45558.2815 | 0.42753 | 0.90739 | 0.001868 | 0.28281 | 8.7603e-07 | 0.10774 | 34278.3234 | 0.73815 | 0.95323 | 0.017902 |  | 0.029125
0.011909 | 6.198e-08 | 0.36622 | 16344.0901 | 0.81007 | 0.91461 | 0.00092686 |  | 0.46857 | 6.286e-08 | 0.88868 | 56044.878 | 0.25227 | 0.88444 | 0.0021943 | 0.69484 | 1.5424e-06 | 0.50219 | 43962.6914 | 0.097087 | 0.86495 | 0.047572 |  | 0.050693
0.4302 | 5.5724e-07 | 0.51678 | 17648.66 | 0.51186 | 0.87309 | 0.010488 |  | 0.93687 | 2.0812e-07 | 0.60486 | 46313.4185 | 0.70406 | 0.93595 | 0.0056785 | 0.99498 | 3.5783e-06 | 0.80563 | 52176.2114 | 0.074289 | 0.85607 | 0.12503 |  | 0.1412
0.97465 | 2.1139e-06 | 0.93771 | 23793.3971 | 0.42533 | 0.86083 | 0.047421 |  | 0.67746 | 9.9496e-08 | 0.14849 | 35646.6752 | 0.64762 | 0.93026 | 0.0022575 | 0.82969 | 1.8906e-06 | 0.17307 | 36372.822 | 0.29095 | 0.90559 | 0.046773 |  | 0.096452
0.66462 | 8.6776e-07 | 0.2707 | 15488.602 | 0.74548 | 0.9049 | 0.01331 |  | 0.94503 | 2.1698e-07 | 0.65949 | 47677.5392 | 0.95484 | 0.96867 | 0.0056059 | 0.41293 | 1.0664e-06 | 0.95574 | 61738.3529 | 0.32766 | 0.9106 | 0.038327 |  | 0.057243
0.50466 | 6.4432e-07 | 0.17124 | 14474.4731 | 0.76503 | 0.90774 | 0.0094402 |  | 0.90498 | 1.8173e-07 | 0.82753 | 53044.7863 | 0.7836 | 0.94431 | 0.0054381 | 0.55314 | 1.2825e-06 | 0.42266 | 42233.9673 | 0.20404 | 0.8915 | 0.036333 |  | 0.051211
0.22503 | 3.3988e-07 | 0.22163 | 15012.8461 | 0.62869 | 0.88884 | 0.0055774 |  | 0.4287 | 5.7229e-08 | 0.283 | 39152.0213 | 0.2204 | 0.87916 | 0.0015908 | 0.27243 | 8.6061e-07 | 0.33744 | 40380.769 | 0.10206 | 0.86664 | 0.025113 |  | 0.032281
0.70937 | 9.4515e-07 | 0.49604 | 17466.0334 | 0.039818 | 0.75536 | 0.026489 |  | 0.56687 | 7.8254e-08 | 0.69086 | 48516.4576 | 0.22783 | 0.88044 | 0.002491 | 0.088479 | 5.4407e-07 | 0.38952 | 41518.0694 | 0.40892 | 0.92048 | 0.014186 |  | 0.043167
0.24152 | 3.57e-07 | 0.037702 | 12263.7007 | 0.63185 | 0.88926 | 0.0054098 |  | 0.24186 | 3.3636e-08 | 0.023538 | 29521.5293 | 0.35738 | 0.89908 | 0.00074374 | 0.20393 | 7.5541e-07 | 0.72971 | 49631.9025 | 0.42414 | 0.92219 | 0.022436 |  | 0.02859
0.15472 | 2.6517e-07 | 0.8418 | 21383.5093 | 0.18657 | 0.81709 | 0.0065655 |  | 0.72387 | 1.1038e-07 | 0.87602 | 55329.8129 | 0.75744 | 0.94149 | 0.0034406 | 0.76431 | 1.702e-06 | 0.14406 | 35509.3148 | 0.74662 | 0.95405 | 0.035682 |  | 0.045688
0.31195 | 4.2999e-07 | 0.88612 | 22275.1942 | 0.62016 | 0.8877 | 0.0084814 |  | 0.34968 | 4.6807e-08 | 0.038829 | 30856.7561 | 0.46486 | 0.91152 | 0.0010211 | 0.58604 | 1.3376e-06 | 0.84834 | 53952.9018 | 0.83595 | 0.96312 | 0.039075 |  | 0.048578
0.94249 | 1.7404e-06 | 0.68119 | 19229.5544 | 0.1688 | 0.8125 | 0.042182 |  | 0.40979 | 5.4655e-08 | 0.14028 | 35389.9575 | 0.86139 | 0.95347 | 0.0011449 | 0.67904 | 1.5099e-06 | 0.55838 | 45223.5012 | 0.63871 | 0.94377 | 0.039658 |  | 0.082985
0.49803 | 6.3625e-07 | 0.22547 | 15051.4485 | 0.62866 | 0.88883 | 0.010452 |  | 0.26353 | 3.622e-08 | 0.57439 | 45593.0762 | 0.45831 | 0.9108 | 0.001035 | 0.2685 | 8.5475e-07 | 0.77584 | 51105.4186 | 0.84237 | 0.96382 | 0.02376 |  | 0.035247
0.99538 | 2.8618e-06 | 0.16633 | 14418.2223 | 0.84974 | 0.92121 | 0.038757 |  | 0.43324 | 5.7856e-08 | 0.034607 | 30533.9868 | 0.072878 | 0.84101 | 0.0015487 | 0.35406 | 9.8035e-07 | 0.75729 | 50489.523 | 0.77628 | 0.95696 | 0.02738 |  | 0.067686
0.47524 | 6.0903e-07 | 0.62429 | 18645.3519 | 0.79726 | 0.9126 | 0.0098443 |  | 0.16874 | 2.4995e-08 | 0.72146 | 49386.8408 | 0.49266 | 0.91449 | 0.00075165 | 0.60365 | 1.3682e-06 | 0.57945 | 45711.229 | 0.26591 | 0.9019 | 0.039961 |  | 0.050557
0.51497 | 6.57e-07 | 0.45386 | 17099.7033 | 0.33112 | 0.84607 | 0.013612 |  | 0.6868 | 1.0157e-07 | 0.3596 | 40867.5566 | 0.49461 | 0.9147 | 0.0026573 | 0.046713 | 4.3556e-07 | 0.83619 | 53411.463 | 0.19456 | 0.88969 | 0.014558 |  | 0.030827
0.59816 | 7.6692e-07 | 0.95177 | 24402.6257 | 0.15235 | 0.80792 | 0.020465 |  | 0.94167 | 2.132e-07 | 0.4179 | 42131.3275 | 0.47967 | 0.91311 | 0.0057236 | 0.99939 | 4.4641e-06 | 0.8727 | 55151.9743 | 0.47684 | 0.92786 | 0.14243 |  | 0.16862
0.63747 | 8.2482e-07 | 0.71949 | 19658.4914 | 0.096351 | 0.78861 | 0.021667 |  | 0.82045 | 1.3973e-07 | 0.64817 | 47385.8085 | 0.68689 | 0.93421 | 0.0038982 | 0.38416 | 1.0242e-06 | 0.71181 | 49105.8456 | 0.59462 | 0.93957 | 0.02905 |  | 0.054615
0.68349 | 8.993e-07 | 0.96735 | 25301.9506 | 0.48537 | 0.86942 | 0.020178 |  | 0.092849 | 1.5776e-08 | 0.98444 | 67581.3566 | 0.84342 | 0.95121 | 0.00057449 | 0.55327 | 1.2827e-06 | 0.69436 | 48613.1226 | 0.99624 | 0.99179 | 0.031844 |  | 0.052596
0.026177 | 9.4498e-08 | 0.91591 | 23054.5766 | 0.39195 | 0.85582 | 0.0021258 |  | 0.44126 | 5.8973e-08 | 0.80697 | 52227.069 | 0.79593 | 0.94568 | 0.001737 | 0.61537 | 1.389e-06 | 0.35848 | 40843.2756 | 0.65677 | 0.94548 | 0.033453 |  | 0.037316
0.8891 | 1.4305e-06 | 0.046387 | 12504.0833 | 0.62294 | 0.88807 | 0.021968 |  | 0.79636 | 1.3125e-07 | 0.39265 | 41585.9302 | 0.088821 | 0.84732 | 0.0040678 | 0.13695 | 6.4151e-07 | 0.26983 | 38845.0338 | 0.64971 | 0.94481 | 0.014874 |  | 0.040909
0.89926 | 1.4766e-06 | 0.90541 | 22756.3229 | 0.6382 | 0.89012 | 0.029168 |  | 0.063427 | 1.1919e-08 | 0.16166 | 36042.9292 | 0.71719 | 0.93729 | 0.0002668 | 0.26211 | 8.4518e-07 | 0.41907 | 42156.5409 | 0.88337 | 0.96855 | 0.019583 |  | 0.049018
0.72301 | 9.707e-07 | 0.88146 | 22169.2891 | 0.76965 | 0.90842 | 0.017561 |  | 0.32309 | 4.3473e-08 | 0.19502 | 36978.3542 | 0.31113 | 0.89305 | 0.0011251 | 0.78992 | 1.7701e-06 | 0.31251 | 39824.9957 | 0.095639 | 0.86444 | 0.051489 |  | 0.070176
0.9242 | 1.6115e-06 | 0.68452 | 19265.6301 | 0.62058 | 0.88775 | 0.029627 |  | 0.52079 | 7.073e-08 | 0.69429 | 48611.1387 | 0.2111 | 0.87751 | 0.0022675 | 0.025756 | 3.5884e-07 | 0.1699 | 36282.4134 | 0.87196 | 0.96718 | 0.0073278 |  | 0.039222
0.91664 | 1.5667e-06 | 0.83916 | 21337.058 | 0.54079 | 0.87703 | 0.031534 |  | 0.4099 | 5.467e-08 | 0.081112 | 33205.6175 | 0.69361 | 0.93489 | 0.0011604 | 0.28339 | 8.769e-07 | 0.18933 | 36824.7796 | 0.62511 | 0.94248 | 0.019636 |  | 0.05233
0.56456 | 7.2073e-07 | 0.20307 | 14821.8321 | 0.26972 | 0.83508 | 0.014872 |  | 0.28234 | 3.8483e-08 | 0.50283 | 43976.7805 | 0.2063 | 0.87664 | 0.0011577 | 0.79942 | 1.7971e-06 | 0.5675 | 45433.4741 | 0.16075 | 0.88261 | 0.054512 |  | 0.070542
0.47186 | 6.0506e-07 | 0.70566 | 19499.6666 | 0.021644 | 0.73461 | 0.0184 |  | 0.71434 | 1.0801e-07 | 0.61028 | 46444.296 | 0.41491 | 0.90595 | 0.0031623 | 0.89452 | 2.151e-06 | 0.42474 | 42278.8581 | 0.33894 | 0.91206 | 0.058042 |  | 0.079604
0.58378 | 7.4681e-07 | 0.76554 | 20228.4943 | 0.89261 | 0.92932 | 0.011644 |  | 0.3708 | 4.9512e-08 | 0.66919 | 47931.8926 | 0.83701 | 0.95043 | 0.0013428 | 0.35179 | 9.7705e-07 | 0.78632 | 51469.5501 | 0.092403 | 0.86329 | 0.033408 |  | 0.046394
0.55859 | 7.128e-07 | 0.31016 | 15849.9569 | 0.77812 | 0.90969 | 0.010778 |  | 0.55295 | 7.5916e-08 | 0.40032 | 41751.6288 | 0.74836 | 0.94053 | 0.001886 | 0.74213 | 1.6476e-06 | 0.53423 | 44675.6241 | 0.83816 | 0.96336 | 0.040743 |  | 0.053407
0.92627 | 1.6245e-06 | 0.28534 | 15624.3935 | 0.85499 | 0.92214 | 0.022783 |  | 0.19201 | 2.7744e-08 | 0.049292 | 31560.059 | 0.59203 | 0.92469 | 0.00058785 | 0.023152 | 3.4697e-07 | 0.93115 | 59093.515 | 0.67487 | 0.94719 | 0.011315 |  | 0.034686
0.0030132 | 3.0332e-08 | 0.57499 | 18175.3388 | 0.013247 | 0.71889 | 0.00094511 |  | 0.31409 | 4.2359e-08 | 0.27965 | 39074.5395 | 0.73666 | 0.93931 | 0.0010026 | 0.42125 | 1.0787e-06 | 0.57516 | 45610.9957 | 0.45633 | 0.9257 | 0.029793 |  | 0.03174
0.90713 | 1.5154e-06 | 0.59224 | 18336.7125 | 0.80166 | 0.91329 | 0.0242 |  | 0.83171 | 1.4407e-07 | 0.16646 | 36183.0867 | 0.44017 | 0.9088 | 0.0035198 | 0.49226 | 1.1857e-06 | 0.69262 | 48565.1161 | 0.55636 | 0.93587 | 0.033606 |  | 0.061326
0.50067 | 6.3946e-07 | 0.2321 | 15117.5465 | 0.35225 | 0.84956 | 0.012533 |  | 0.68677 | 1.0156e-07 | 0.3205 | 40004.1249 | 0.21336 | 0.87792 | 0.0028696 | 0.42951 | 1.0909e-06 | 0.6634 | 47779.4634 | 0.73824 | 0.95323 | 0.029311 |  | 0.044714
0.44875 | 5.7828e-07 | 0.41373 | 16754.2433 | 0.95443 | 0.94509 | 0.0073601 |  | 0.071861 | 1.3055e-08 | 0.52197 | 44401.0279 | 0.94732 | 0.96703 | 0.00031797 | 0.65338 | 1.4594e-06 | 0.41419 | 42051.3158 | 0.72656 | 0.95211 | 0.035337 |  | 0.043015
0.13671 | 2.4519e-07 | 0.40281 | 16660.3343 | 0.45575 | 0.86524 | 0.0046617 |  | 0.5942 | 8.3031e-08 | 0.45498 | 42932.4088 | 0.8129 | 0.9476 | 0.0020701 | 0.23836 | 8.0917e-07 | 0.78717 | 51499.4418 | 0.54229 | 0.93449 | 0.024115 |  | 0.030847
0.45246 | 5.8254e-07 | 0.55758 | 18015.1183 | 0.033926 | 0.74977 | 0.016704 |  | 0.90099 | 1.7906e-07 | 0.79804 | 51892.497 | 0.79151 | 0.94518 | 0.005251 | 0.54099 | 1.2627e-06 | 0.15109 | 35726.3928 | 0.76653 | 0.95599 | 0.02643 |  | 0.048385
0.21152 | 3.2578e-07 | 0.16085 | 14354.373 | 0.51847 | 0.874 | 0.0056396 |  | 0.9675 | 2.5031e-07 | 0.83975 | 53567.0755 | 0.72026 | 0.93761 | 0.0076539 | 0.42323 | 1.0816e-06 | 0.15916 | 35969.0577 | 0.18666 | 0.88813 | 0.027875 |  | 0.041169
0.031519 | 1.0459e-07 | 0.66033 | 19009.0877 | 0.14241 | 0.80496 | 0.0025873 |  | 0.98412 | 2.9513e-07 | 0.95473 | 61606.3206 | 0.45589 | 0.91054 | 0.010591 | 0.66825 | 1.4883e-06 | 0.22353 | 37719.4949 | 0.64086 | 0.94397 | 0.033801 |  | 0.046979
0.43123 | 5.584e-07 | 0.50768 | 17568.3174 | 0.64286 | 0.89074 | 0.0097137 |  | 0.52415 | 7.1259e-08 | 0.096166 | 33835.2347 | 0.44178 | 0.90898 | 0.001664 | 0.52738 | 1.2408e-06 | 0.80965 | 52329.7149 | 0.5771 | 0.93789 | 0.0372 |  | 0.048577
0.79866 | 1.136e-06 | 0.79658 | 20658.8024 | 0.93356 | 0.93886 | 0.017101 |  | 0.73946 | 1.144e-07 | 0.52869 | 44551.2754 | 0.26043 | 0.88571 | 0.0034024 | 0.80809 | 1.8226e-06 | 0.83163 | 53216.4476 | 0.57378 | 0.93756 | 0.055437 |  | 0.075941
0.89333 | 1.4491e-06 | 0.0069682 | 10702.3665 | 0.43338 | 0.86201 | 0.024202 |  | 0.11034 | 1.7964e-08 | 0.29542 | 39437.6873 | 0.5695 | 0.92242 | 0.00044882 | 0.22443 | 7.8768e-07 | 0.34788 | 40610.9184 | 0.094031 | 0.86387 | 0.02321 |  | 0.047861
0.77997 | 1.0907e-06 | 0.10623 | 13638.1977 | 0.75586 | 0.9064 | 0.015684 |  | 0.599 | 8.3899e-08 | 0.080703 | 33187.4689 | 0.92988 | 0.96367 | 0.0016086 | 0.5441 | 1.2677e-06 | 0.65165 | 47474.7864 | 0.51007 | 0.93127 | 0.035656 |  | 0.052948
0.13933 | 2.4812e-07 | 0.30958 | 15844.745 | 0.87514 | 0.92585 | 0.0034316 |  | 0.2743 | 3.7513e-08 | 0.084048 | 33333.9271 | 0.9936 | 0.98275 | 0.00067114 | 0.49048 | 1.1829e-06 | 0.9443 | 60377.9735 | 0.3545 | 0.91403 | 0.04155 |  | 0.045653
0.60468 | 7.7621e-07 | 0.059037 | 12802.7827 | 0.77159 | 0.90871 | 0.010722 |  | 0.89998 | 1.784e-07 | 0.24622 | 38281.2545 | 0.012074 | 0.78972 | 0.0059828 | 0.14493 | 6.5601e-07 | 0.1526 | 35772.3276 | 0.29471 | 0.90612 | 0.016027 |  | 0.032732
0.3226 | 4.4112e-07 | 0.45325 | 17094.468 | 0.2447 | 0.83014 | 0.0096938 |  | 0.79284 | 1.3009e-07 | 0.090711 | 33614.8224 | 0.84574 | 0.9515 | 0.002633 | 0.10357 | 5.7653e-07 | 0.63877 | 47147.4001 | 0.18718 | 0.88824 | 0.017717 |  | 0.030043
0.14153 | 2.5058e-07 | 0.31066 | 15854.3831 | 0.012421 | 0.71688 | 0.0076388 |  | 0.060358 | 1.1498e-08 | 0.5495 | 45020.7478 | 0.23572 | 0.88176 | 0.00034733 | 0.9218 | 2.3058e-06 | 0.29533 | 39435.5685 | 0.028022 | 0.82587 | 0.072722 |  | 0.080709
0.11206 | 2.1682e-07 | 0.75115 | 20042.8076 | 0.99695 | 0.9722 | 0.0026403 |  | 0.80637 | 1.3465e-07 | 0.94989 | 61008.1669 | 0.72475 | 0.93807 | 0.0045836 | 0.33558 | 9.5345e-07 | 0.15245 | 35767.7614 | 0.13216 | 0.87559 | 0.025321 |  | 0.032545
0.40367 | 5.2777e-07 | 0.98291 | 26731.3989 | 0.28833 | 0.83857 | 0.013379 |  | 0.34885 | 4.6703e-08 | 0.40914 | 41942.3192 | 0.96428 | 0.97097 | 0.0010697 | 0.74085 | 1.6446e-06 | 0.29005 | 39314.6489 | 0.81731 | 0.96114 | 0.03667 |  | 0.051118
0.56766 | 7.2487e-07 | 0.78307 | 20466.0739 | 0.35522 | 0.85004 | 0.015827 |  | 0.80634 | 1.3464e-07 | 0.2573 | 38547.9929 | 0.70508 | 0.93606 | 0.0031833 | 0.2495 | 8.2616e-07 | 0.8335 | 53295.8673 | 0.099123 | 0.86565 | 0.028781 |  | 0.047791
0.84577 | 1.2695e-06 | 0.49785 | 17481.9189 | 0.19569 | 0.81931 | 0.029187 |  | 0.14229 | 2.1846e-08 | 0.7297 | 49631.3892 | 0.43765 | 0.90852 | 0.00066758 | 0.10933 | 5.8835e-07 | 0.013749 | 28257.7585 | 0.60196 | 0.94027 | 0.010894 |  | 0.040749
0.023661 | 8.9453e-08 | 0.92186 | 23237.8907 | 0.036969 | 0.75275 | 0.0027198 |  | 0.7868 | 1.2813e-07 | 0.60926 | 46419.624 | 0.57593 | 0.92307 | 0.0036086 | 0.20353 | 7.5476e-07 | 0.063188 | 32347.427 | 0.75699 | 0.95506 | 0.01463 |  | 0.020959
0.22966 | 3.4469e-07 | 0.20684 | 14861.2126 | 0.8156 | 0.91549 | 0.0048964 |  | 0.065061 | 1.2141e-08 | 0.57367 | 45576.4838 | 0.49541 | 0.91478 | 0.00034374 | 0.34887 | 9.728e-07 | 0.67365 | 48050.2975 | 0.60793 | 0.94084 | 0.02703 |  | 0.03227
0.94166 | 1.7338e-06 | 0.54878 | 17935.0848 | 0.61424 | 0.8869 | 0.030967 |  | 0.85331 | 1.5322e-07 | 0.31819 | 39952.4279 | 0.75098 | 0.94081 | 0.0036741 | 0.33266 | 9.4919e-07 | 0.46019 | 43045.2567 | 0.37642 | 0.9167 | 0.025654 |  | 0.060295
0.4373 | 5.6525e-07 | 0.68623 | 19284.1567 | 0.37687 | 0.85348 | 0.011907 |  | 0.89518 | 1.7534e-07 | 0.31298 | 39835.5612 | 0.8729 | 0.95499 | 0.0040265 | 0.91912 | 2.2887e-06 | 0.23142 | 37917.2588 | 0.89836 | 0.97043 | 0.048035 |  | 0.063968
0.93273 | 1.6675e-06 | 0.63582 | 18759.6252 | 0.32799 | 0.84554 | 0.035787 |  | 0.025935 | 6.3181e-09 | 0.3885 | 41496.0764 | 0.57965 | 0.92345 | 0.00016342 | 0.95863 | 2.6209e-06 | 0.67588 | 48109.7434 | 0.22958 | 0.89605 | 0.080358 |  | 0.11631
0.66878 | 8.7459e-07 | 0.24794 | 15272.4016 | 0.15051 | 0.80738 | 0.020149 |  | 0.41095 | 5.4812e-08 | 0.35248 | 40711.8315 | 0.9988 | 0.98921 | 0.0011555 | 0.27726 | 8.6781e-07 | 0.063715 | 32374.8261 | 0.12267 | 0.87297 | 0.02192 |  | 0.043225
0.027553 | 9.7173e-08 | 0.26358 | 15421.6601 | 0.92804 | 0.93741 | 0.0012352 |  | 0.98003 | 2.8085e-07 | 0.19702 | 37032.0552 | 0.54193 | 0.91962 | 0.0067599 | 0.32655 | 9.4027e-07 | 0.57916 | 45704.4429 | 0.88293 | 0.9685 | 0.023405 |  | 0.0314
0.06732 | 1.6027e-07 | 0.235 | 15146.2158 | 0.87963 | 0.92672 | 0.0021536 |  | 0.050367 | 1.0094e-08 | 0.8608 | 54545.0207 | 0.27327 | 0.88766 | 0.0003437 | 0.99389 | 3.4936e-06 | 0.8898 | 56111.0584 | 0.95955 | 0.97994 | 0.10219 |  | 0.10469
0.34131 | 4.6077e-07 | 0.77992 | 20422.3746 | 0.81905 | 0.91605 | 0.0076984 |  | 0.22973 | 3.2198e-08 | 0.045612 | 31326.0184 | 0.36094 | 0.89952 | 0.00073705 | 0.80071 | 1.8008e-06 | 0.02166 | 29315.6237 | 0.40402 | 0.91992 | 0.036914 |  | 0.04535
0.70956 | 9.4549e-07 | 0.97726 | 26108.7457 | 0.93445 | 0.93909 | 0.016636 |  | 0.038202 | 8.2917e-09 | 0.73493 | 49789.5496 | 0.098735 | 0.85077 | 0.00028401 | 0.010457 | 2.7211e-07 | 0.86853 | 54934.1239 | 0.6199 | 0.94199 | 0.0084233 |  | 0.025343
0.47388 | 6.0743e-07 | 0.72172 | 19684.6185 | 0.10975 | 0.79392 | 0.015712 |  | 0.33111 | 4.4471e-08 | 0.48888 | 43670.4421 | 0.28391 | 0.88922 | 0.001295 | 0.79734 | 1.7911e-06 | 0.18903 | 36816.5813 | 0.58626 | 0.93877 | 0.04056 |  | 0.057567
0.4558 | 5.8638e-07 | 0.68397 | 19259.5776 | 0.33529 | 0.84677 | 0.012652 |  | 0.68355 | 1.0084e-07 | 0.57896 | 45699.6054 | 0.653 | 0.9308 | 0.002756 | 0.65041 | 1.4537e-06 | 0.44159 | 42642.8199 | 0.65805 | 0.9456 | 0.036237 |  | 0.051645
0.29205 | 4.0931e-07 | 0.38548 | 16510.8965 | 0.070429 | 0.7763 | 0.010644 |  | 0.96744 | 2.502e-07 | 0.25143 | 38407.2223 | 0.80178 | 0.94633 | 0.0057231 | 0.069594 | 4.9935e-07 | 0.15042 | 35705.85 | 0.13854 | 0.87726 | 0.01319 |  | 0.029557
0.87698 | 1.3803e-06 | 0.76181 | 20179.6454 | 0.86859 | 0.92462 | 0.021992 |  | 0.01381 | 4.087e-09 | 0.37337 | 41167.8819 | 0.76424 | 0.94222 | 9.9953e-05 | 0.11427 | 5.9824e-07 | 0.67751 | 48153.4461 | 0.16228 | 0.88296 | 0.018852 |  | 0.040944
0.057846 | 1.4689e-07 | 0.3373 | 16091.2743 | 0.51001 | 0.87284 | 0.0026679 |  | 0.091599 | 1.5617e-08 | 0.54858 | 44999.9652 | 0.9933 | 0.98252 | 0.00036916 | 0.050645 | 4.4757e-07 | 0.12588 | 34918.872 | 0.079803 | 0.85842 | 0.012259 |  | 0.015296
0.96692 | 1.9938e-06 | 0.044842 | 12463.8458 | 0.10537 | 0.79224 | 0.046129 |  | 0.51901 | 7.0451e-08 | 0.1267 | 34946.675 | 0.033984 | 0.81809 | 0.0021297 | 0.70047 | 1.5542e-06 | 0.034948 | 30561.0658 | 0.81295 | 0.96068 | 0.028169 |  | 0.076428
0.80984 | 1.1649e-06 | 0.064989 | 12928.1517 | 0.16751 | 0.81215 | 0.025285 |  | 0.26811 | 3.6769e-08 | 0.79997 | 51963.6551 | 0.2709 | 0.8873 | 0.0012107 | 0.49583 | 1.1912e-06 | 0.53759 | 44751.0952 | 0.62449 | 0.94242 | 0.031127 |  | 0.057623
0.80786 | 1.1597e-06 | 0.0010762 | 9474.2253 | 0.33848 | 0.8473 | 0.020167 |  | 0.91887 | 1.9198e-07 | 0.26667 | 38770.4971 | 0.64275 | 0.92977 | 0.0046412 | 0.78164 | 1.7474e-06 | 0.1955 | 36991.3537 | 0.77765 | 0.95709 | 0.037501 |  | 0.062309
0.2758 | 3.9248e-07 | 0.51674 | 17648.3269 | 0.26561 | 0.83429 | 0.0085865 |  | 0.44164 | 5.9026e-08 | 0.080852 | 33194.0801 | 0.043508 | 0.8253 | 0.0017118 | 0.19675 | 7.4388e-07 | 0.5003 | 43921.1116 | 0.88594 | 0.96886 | 0.017856 |  | 0.028155
0.76538 | 1.0576e-06 | 0.55239 | 17967.8776 | 0.78854 | 0.91126 | 0.016879 |  | 0.050843 | 1.0162e-08 | 0.18253 | 36638.0712 | 0.97328 | 0.97352 | 0.0002048 | 0.42804 | 1.0887e-06 | 0.83955 | 53557.8892 | 0.61245 | 0.94128 | 0.033043 |  | 0.050127
0.72918 | 9.8262e-07 | 0.90657 | 22787.9058 | 0.73022 | 0.90273 | 0.01848 |  | 0.087077 | 1.504e-08 | 0.45258 | 42880.3554 | 0.50633 | 0.91593 | 0.0004061 | 0.26418 | 8.4829e-07 | 0.26349 | 38695.3806 | 0.40352 | 0.91987 | 0.021052 |  | 0.039938
0.90859 | 1.523e-06 | 0.78361 | 20473.5641 | 0.25703 | 0.83262 | 0.035311 |  | 0.60091 | 8.4246e-08 | 0.55952 | 45249.7109 | 0.9929 | 0.98222 | 0.0020034 | 0.15405 | 6.7221e-07 | 0.26852 | 38814.1075 | 0.0034062 | 0.76824 | 0.02367 |  | 0.060984
0.91408 | 1.5523e-06 | 0.89291 | 22436.086 | 0.7609 | 0.90714 | 0.028425 |  | 0.7075 | 1.0636e-07 | 0.14742 | 35613.7585 | 0.31194 | 0.89316 | 0.0026871 | 0.59653 | 1.3557e-06 | 0.39438 | 41623.2231 | 0.35279 | 0.91381 | 0.036019 |  | 0.067131
0.88659 | 1.4197e-06 | 0.57556 | 18180.6274 | 0.52403 | 0.87476 | 0.026864 |  | 0.53709 | 7.3323e-08 | 0.14053 | 35398.1572 | 0.77092 | 0.94293 | 0.0015902 | 0.93623 | 2.4087e-06 | 0.14506 | 35540.4905 | 0.51982 | 0.93226 | 0.054198 |  | 0.082652
0.38431 | 5.0667e-07 | 0.55624 | 18002.8969 | 0.31952 | 0.8441 | 0.010769 |  | 0.4673 | 6.2677e-08 | 0.28196 | 39127.9193 | 0.87689 | 0.95552 | 0.0014159 | 0.51019 | 1.2136e-06 | 0.43799 | 42564.8715 | 0.13767 | 0.87703 | 0.035724 |  | 0.047909
0.44921 | 5.788e-07 | 0.45301 | 17092.394 | 0.045582 | 0.76018 | 0.01592 |  | 0.29628 | 4.0176e-08 | 0.71522 | 49204.404 | 0.80083 | 0.94622 | 0.0011245 | 0.15578 | 6.7525e-07 | 0.91797 | 58006.0987 | 0.65339 | 0.94516 | 0.021754 |  | 0.038799
0.33886 | 4.5818e-07 | 0.022979 | 11741.0366 | 0.24309 | 0.82981 | 0.009063 |  | 0.40134 | 5.3522e-08 | 0.32026 | 39998.8952 | 0.63745 | 0.92924 | 0.0013264 | 0.055984 | 4.6308e-07 | 0.96309 | 62789.0911 | 0.92774 | 0.9745 | 0.015202 |  | 0.025591
0.30977 | 4.2772e-07 | 0.35215 | 16221.5545 | 0.37384 | 0.85301 | 0.0084669 |  | 0.064958 | 1.2128e-08 | 0.7803 | 51258.8336 | 0.6783 | 0.93334 | 0.00036092 | 0.93005 | 2.3623e-06 | 0.97142 | 64242.7525 | 0.52396 | 0.93267 | 0.084706 |  | 0.093534
0.87902 | 1.3884e-06 | 0.6704 | 19114.4771 | 0.97925 | 0.95554 | 0.018087 |  | 0.77815 | 1.2543e-07 | 0.31329 | 39842.6179 | 0.53742 | 0.91915 | 0.003185 | 0.21981 | 7.8049e-07 | 0.39577 | 41653.4567 | 0.41175 | 0.9208 | 0.020383 |  | 0.041654
0.51319 | 6.548e-07 | 0.51558 | 17638.0157 | 0.43035 | 0.86156 | 0.012916 |  | 0.7455 | 1.1602e-07 | 0.96402 | 62935.7612 | 0.49614 | 0.91486 | 0.0042053 | 0.41357 | 1.0673e-06 | 0.014796 | 28421.4032 | 0.086961 | 0.86126 | 0.026035 |  | 0.043157
0.14282 | 2.5203e-07 | 0.37152 | 16390.1007 | 0.21116 | 0.82292 | 0.0056092 |  | 0.42228 | 5.635e-08 | 0.12842 | 35004.2476 | 0.90553 | 0.95965 | 0.0011456 | 0.85969 | 1.998e-06 | 0.81101 | 52382.2429 | 0.020118 | 0.81621 | 0.074882 |  | 0.081637
0.94009 | 1.7215e-06 | 0.77083 | 20298.7662 | 0.94361 | 0.94168 | 0.025248 |  | 0.55839 | 7.6822e-08 | 0.24902 | 38349.0514 | 0.38534 | 0.90249 | 0.0019856 | 0.068493 | 4.9656e-07 | 0.56491 | 45373.6248 | 0.40158 | 0.91964 | 0.013856 |  | 0.041089
0.85243 | 1.2913e-06 | 0.27792 | 15555.8762 | 0.74104 | 0.90426 | 0.019912 |  | 0.038637 | 8.3584e-09 | 0.6534 | 47519.7854 | 0.79107 | 0.94514 | 0.00022787 | 0.52823 | 1.2421e-06 | 0.38021 | 41316.3776 | 0.5464 | 0.93489 | 0.031074 |  | 0.051214
0.92907 | 1.6427e-06 | 0.12615 | 13919.4668 | 0.81799 | 0.91588 | 0.022576 |  | 0.54187 | 7.4097e-08 | 0.96151 | 62547.885 | 0.15777 | 0.8668 | 0.0028732 | 0.75835 | 1.687e-06 | 0.22135 | 37664.5375 | 0.8093 | 0.9603 | 0.036376 |  | 0.061825
0.64304 | 8.3341e-07 | 0.30566 | 15809.4362 | 0.57534 | 0.88169 | 0.014446 |  | 0.38223 | 5.0999e-08 | 0.48646 | 43617.3493 | 0.077216 | 0.84284 | 0.0016395 | 0.40301 | 1.0518e-06 | 0.1041 | 34142.1806 | 0.33982 | 0.91218 | 0.024471 |  | 0.040556
0.13747 | 2.4604e-07 | 0.95786 | 24717.6185 | 0.7411 | 0.90427 | 0.0048129 |  | 0.030559 | 7.0858e-09 | 0.3509 | 40677.0576 | 0.032934 | 0.81719 | 0.00023124 | 0.53824 | 1.2582e-06 | 0.72166 | 49392.67 | 0.47811 | 0.92799 | 0.036772 |  | 0.041816
0.50879 | 6.4937e-07 | 0.28976 | 15665.0192 | 0.72522 | 0.90202 | 0.010161 |  | 0.83402 | 1.45e-07 | 0.4086 | 41930.5665 | 0.11214 | 0.855 | 0.0044409 | 0.91462 | 2.2609e-06 | 0.70061 | 48787.4547 | 0.79592 | 0.95893 | 0.061021 |  | 0.075623
0.12759 | 2.3485e-07 | 0.39454 | 16589.0898 | 0.53465 | 0.8762 | 0.0042537 |  | 0.62296 | 8.8359e-08 | 0.39939 | 41731.6681 | 0.17763 | 0.87108 | 0.0026039 | 0.14329 | 6.5306e-07 | 0.30444 | 39642.8994 | 0.14533 | 0.87897 | 0.018302 |  | 0.02516
0.15141 | 2.6153e-07 | 0.2022 | 14812.7704 | 0.17994 | 0.81541 | 0.0058084 |  | 0.39976 | 5.3312e-08 | 0.85494 | 54261.8129 | 0.053065 | 0.83123 | 0.0019905 | 0.76925 | 1.7147e-06 | 0.48862 | 43664.7357 | 0.77765 | 0.95709 | 0.042274 |  | 0.050073
0.28298 | 3.9991e-07 | 0.66346 | 19041.6697 | 0.55127 | 0.87845 | 0.0076027 |  | 0.79417 | 1.3052e-07 | 0.62825 | 46884.6797 | 0.95822 | 0.96946 | 0.0033155 | 0.78443 | 1.755e-06 | 0.80333 | 52089.1833 | 0.78232 | 0.95756 | 0.050293 |  | 0.061211
0.23317 | 3.4833e-07 | 0.62477 | 18650.1234 | 0.21277 | 0.82328 | 0.0080665 |  | 0.62286 | 8.834e-08 | 0.11314 | 34475.2637 | 0.34443 | 0.89744 | 0.0021603 | 0.033504 | 3.9039e-07 | 0.52697 | 44512.8184 | 0.59709 | 0.93981 | 0.010224 |  | 0.020451
0.45545 | 5.8597e-07 | 0.60116 | 18421.479 | 0.68138 | 0.89595 | 0.010177 |  | 0.36385 | 4.8616e-08 | 0.24659 | 38290.1394 | 0.15868 | 0.867 | 0.0013734 | 0.21131 | 7.6712e-07 | 0.61824 | 46638.1307 | 0.21664 | 0.8938 | 0.023126 |  | 0.034676
0.39263 | 5.1571e-07 | 0.55469 | 17988.7591 | 0.55462 | 0.8789 | 0.0095473 |  | 0.82445 | 1.4125e-07 | 0.57044 | 45501.3788 | 0.15204 | 0.86548 | 0.0044456 | 0.65152 | 1.4558e-06 | 0.27482 | 38961.9183 | 0.59034 | 0.93916 | 0.034394 |  | 0.048387
0.19949 | 3.1316e-07 | 0.77153 | 20308.2253 | 0.84092 | 0.91968 | 0.0051278 |  | 0.24135 | 3.3575e-08 | 0.17865 | 36530.1987 | 0.13132 | 0.86037 | 0.00093831 | 0.77903 | 1.7404e-06 | 0.50033 | 43921.7147 | 0.379 | 0.91701 | 0.047702 |  | 0.053768
0.96702 | 1.9952e-06 | 0.51598 | 17641.5397 | 0.019704 | 0.73154 | 0.059795 |  | 0.28299 | 3.8562e-08 | 0.90086 | 56800.0812 | 0.11677 | 0.85636 | 0.0014231 | 0.4283 | 1.0891e-06 | 0.20054 | 37125.5378 | 0.15342 | 0.88092 | 0.02917 |  | 0.090388
0.11603 | 2.2148e-07 | 0.038523 | 12288.0316 | 0.88853 | 0.92849 | 0.002651 |  | 0.83919 | 1.4711e-07 | 0.35153 | 40690.985 | 0.81406 | 0.94773 | 0.0035102 | 0.99942 | 4.4863e-06 | 0.23673 | 38048.9558 | 0.49712 | 0.92996 | 0.1069 |  | 0.11306
0.49234 | 6.2938e-07 | 0.80118 | 20726.509 | 0.74885 | 0.90539 | 0.011122 |  | 0.081365 | 1.4303e-08 | 0.3595 | 40865.41 | 0.7933 | 0.94538 | 0.00034471 | 0.85518 | 1.9807e-06 | 0.92664 | 58702.5329 | 0.16811 | 0.88425 | 0.071491 |  | 0.082958
0.41565 | 5.41e-07 | 0.61765 | 18580.4454 | 0.31716 | 0.84369 | 0.011648 |  | 0.053731 | 1.0573e-08 | 0.057054 | 32016.3244 | 0.64833 | 0.93033 | 0.000222 | 0.68366 | 1.5192e-06 | 0.85696 | 54358.0827 | 0.97769 | 0.98413 | 0.042748 |  | 0.054619
0.38146 | 5.0359e-07 | 0.10936 | 13684.3749 | 0.49825 | 0.87121 | 0.0086833 |  | 0.004754 | 1.9782e-09 | 0.51693 | 44288.9588 | 0.13489 | 0.86129 | 6.1767e-05 | 0.20719 | 7.606e-07 | 0.82541 | 52957.1342 | 0.84465 | 0.96407 | 0.02181 |  | 0.030555
0.045104 | 1.276e-07 | 0.6674 | 19082.9389 | 0.92343 | 0.93625 | 0.0018525 |  | 0.13243 | 2.0659e-08 | 0.95168 | 61222.8174 | 0.21348 | 0.87794 | 0.00077612 | 0.83525 | 1.9092e-06 | 0.084711 | 33362.5051 | 0.15341 | 0.88091 | 0.047972 |  | 0.050601
0.7033 | 9.3409e-07 | 0.45464 | 17106.4086 | 0.93189 | 0.93841 | 0.012537 |  | 0.95543 | 2.3033e-07 | 0.43659 | 42534.7285 | 0.11451 | 0.8557 | 0.0071032 | 0.40433 | 1.0537e-06 | 0.96486 | 63071.8954 | 0.53568 | 0.93384 | 0.03714 |  | 0.05678
0.25243 | 3.683e-07 | 0.13864 | 14082.8463 | 0.35035 | 0.84925 | 0.007066 |  | 0.81467 | 1.376e-07 | 0.73777 | 49875.998 | 0.83528 | 0.95023 | 0.0038608 | 0.54056 | 1.262e-06 | 0.24503 | 38252.2697 | 0.84045 | 0.96361 | 0.027281 |  | 0.038208
0.28802 | 4.0513e-07 | 0.021615 | 11680.8059 | 0.76891 | 0.90832 | 0.005403 |  | 0.93922 | 2.1056e-07 | 0.46347 | 43116.4594 | 0.8932 | 0.95781 | 0.0051259 | 0.84781 | 1.9534e-06 | 0.18407 | 36680.8784 | 0.31253 | 0.90859 | 0.048193 |  | 0.058721
0.12441 | 2.312e-07 | 0.39308 | 16576.451 | 0.48181 | 0.86892 | 0.0043198 |  | 0.67 | 9.7878e-08 | 0.33177 | 40255.2525 | 0.31913 | 0.89413 | 0.0026692 | 0.92317 | 2.3148e-06 | 0.98905 | 69452.8528 | 0.37616 | 0.91667 | 0.090586 |  | 0.097575
0.7247 | 9.7393e-07 | 0.69077 | 19333.6852 | 0.16367 | 0.81111 | 0.023752 |  | 0.8239 | 1.4103e-07 | 0.67904 | 48194.6841 | 0.50371 | 0.91566 | 0.0041539 | 0.63433 | 1.4235e-06 | 0.52629 | 44497.6122 | 0.82418 | 0.96186 | 0.035219 |  | 0.063125
0.68473 | 9.0142e-07 | 0.93516 | 23696.109 | 0.31255 | 0.84289 | 0.021408 |  | 0.66335 | 9.6464e-08 | 0.66881 | 47921.7661 | 0.57613 | 0.92309 | 0.0027835 | 0.87406 | 2.0567e-06 | 0.47559 | 43380.063 | 0.39128 | 0.91845 | 0.055663 |  | 0.079855
0.8901 | 1.4348e-06 | 0.71578 | 19615.3764 | 0.92549 | 0.93676 | 0.02113 |  | 0.87056 | 1.6149e-07 | 0.48054 | 43488.0171 | 0.16452 | 0.8683 | 0.0049122 | 0.081835 | 5.2894e-07 | 0.50728 | 44075.183 | 0.78782 | 0.95811 | 0.013109 |  | 0.039152
0.60456 | 7.7603e-07 | 0.22942 | 15090.9279 | 0.75319 | 0.90601 | 0.011694 |  | 0.31961 | 4.304e-08 | 0.65524 | 47567.2143 | 0.91637 | 0.96136 | 0.0011298 | 0.14407 | 6.5447e-07 | 0.37491 | 41201.3327 | 0.7189 | 0.95137 | 0.015615 |  | 0.028439
0.12372 | 2.304e-07 | 0.62719 | 18673.9259 | 0.12497 | 0.79935 | 0.0057694 |  | 0.20897 | 2.9744e-08 | 0.86412 | 54710.1135 | 0.63156 | 0.92865 | 0.0009415 | 0.4175 | 1.0731e-06 | 0.337 | 40370.9914 | 0.44683 | 0.92468 | 0.027111 |  | 0.033822
0.22855 | 3.4353e-07 | 0.72387 | 19709.8711 | 0.48563 | 0.86946 | 0.006872 |  | 0.27451 | 3.7538e-08 | 0.24755 | 38313.3889 | 0.21273 | 0.8778 | 0.0010331 | 0.38383 | 1.0237e-06 | 0.28723 | 39249.7086 | 0.20077 | 0.89088 | 0.027684 |  | 0.035589
0.9051 | 1.5051e-06 | 0.42092 | 16816.1191 | 0.97202 | 0.95191 | 0.018387 |  | 0.15955 | 2.3904e-08 | 0.8132 | 52467.593 | 0.38901 | 0.90293 | 0.00076949 | 0.13547 | 6.3878e-07 | 0.25237 | 38429.8674 | 0.025298 | 0.82286 | 0.020012 |  | 0.039169
0.32538 | 4.4403e-07 | 0.99422 | 29000.1007 | 0.53521 | 0.87628 | 0.010454 |  | 0.93938 | 2.1073e-07 | 0.48072 | 43491.826 | 0.23816 | 0.88217 | 0.0062176 | 0.21666 | 7.7556e-07 | 0.84244 | 53686.0644 | 0.33176 | 0.91114 | 0.025006 |  | 0.041677
0.76126 | 1.0486e-06 | 0.49921 | 17493.8307 | 0.58177 | 0.88255 | 0.018883 |  | 0.040948 | 8.7094e-09 | 0.73094 | 49668.6232 | 0.88006 | 0.95596 | 0.00024037 | 0.74888 | 1.6638e-06 | 0.59269 | 46022.9337 | 0.53354 | 0.93362 | 0.045418 |  | 0.064541
0.71303 | 9.5189e-07 | 0.43601 | 16945.9284 | 0.92793 | 0.93738 | 0.012782 |  | 0.99336 | 3.4901e-07 | 0.55327 | 45106.6857 | 0.14246 | 0.86319 | 0.010977 | 0.0495 | 4.4413e-07 | 0.6959 | 48655.8911 | 0.33467 | 0.91151 | 0.013291 |  | 0.03705
0.63012 | 8.1363e-07 | 0.32553 | 15987.1422 | 0.10078 | 0.79043 | 0.020078 |  | 0.65234 | 9.4174e-08 | 0.78618 | 51464.6213 | 0.17689 | 0.87092 | 0.0031753 | 0.41584 | 1.0707e-06 | 0.086313 | 33430.9294 | 0.69763 | 0.94935 | 0.021741 |  | 0.044994
0.20079 | 3.1453e-07 | 0.5397 | 17853.1421 | 0.80149 | 0.91326 | 0.0049541 |  | 0.47967 | 6.4483e-08 | 0.70941 | 49037.0636 | 0.096283 | 0.84995 | 0.0021914 | 0.51051 | 1.2141e-06 | 0.72224 | 49409.7355 | 0.02505 | 0.82257 | 0.043542 |  | 0.050688
0.51697 | 6.5948e-07 | 0.67098 | 19120.6299 | 0.39299 | 0.85597 | 0.013717 |  | 0.61229 | 8.6344e-08 | 0.29941 | 39528.61 | 0.32655 | 0.89512 | 0.0023208 | 0.23885 | 8.0993e-07 | 0.34366 | 40517.9401 | 0.036971 | 0.83416 | 0.025454 |  | 0.041492
0.86085 | 1.3202e-06 | 0.75641 | 20109.6919 | 0.63114 | 0.88917 | 0.024621 |  | 0.85739 | 1.5509e-07 | 0.69196 | 48546.8268 | 0.94684 | 0.96693 | 0.0040894 | 0.20098 | 7.5068e-07 | 0.19249 | 36910.4272 | 0.5194 | 0.93221 | 0.017373 |  | 0.046083
0.43365 | 5.6113e-07 | 0.19701 | 14757.8382 | 0.58637 | 0.88317 | 0.0093995 |  | 0.90767 | 1.836e-07 | 0.13669 | 35275.2846 | 0.85123 | 0.95218 | 0.0038525 | 0.1585 | 6.7998e-07 | 0.96914 | 63810.1123 | 0.2972 | 0.90647 | 0.025237 |  | 0.038489
0.047615 | 1.3155e-07 | 0.85257 | 21579.6527 | 0.76896 | 0.90832 | 0.0023457 |  | 0.85805 | 1.554e-07 | 0.90362 | 56982.3451 | 0.12545 | 0.8588 | 0.0057246 | 0.36465 | 9.9578e-07 | 0.35643 | 40798.2407 | 0.34546 | 0.91289 | 0.026142 |  | 0.034212
0.90721 | 1.5158e-06 | 0.37458 | 16416.6212 | 0.036008 | 0.75183 | 0.042308 |  | 0.62083 | 8.7954e-08 | 0.11886 | 34677.9073 | 0.88383 | 0.95648 | 0.001794 | 0.043681 | 4.2591e-07 | 0.28778 | 39262.3947 | 0.76253 | 0.9556 | 0.0096465 |  | 0.053748
0.2538 | 3.6971e-07 | 0.38836 | 16535.7674 | 0.89485 | 0.92978 | 0.0051162 |  | 0.69489 | 1.0341e-07 | 0.57679 | 45648.9615 | 0.71213 | 0.93678 | 0.0027837 | 0.55727 | 1.2893e-06 | 0.39614 | 41661.4356 | 0.40604 | 0.92016 | 0.033729 |  | 0.041629
0.60112 | 7.7111e-07 | 0.53137 | 17778.4823 | 0.64501 | 0.89103 | 0.013469 |  | 0.087625 | 1.511e-08 | 0.34975 | 40651.9984 | 0.62838 | 0.92834 | 0.00037997 | 0.28581 | 8.8048e-07 | 0.90015 | 56754.0268 | 0.32135 | 0.90977 | 0.029691 |  | 0.043539
0.78427 | 1.1008e-06 | 0.57695 | 18193.5042 | 0.5612 | 0.87979 | 0.020402 |  | 0.64355 | 9.2391e-08 | 0.44985 | 42821.2582 | 0.92838 | 0.9634 | 0.0022019 | 0.83142 | 1.8963e-06 | 0.92661 | 58700.6103 | 0.70085 | 0.94965 | 0.061219 |  | 0.083822
0.66896 | 8.7489e-07 | 0.88817 | 22323.0111 | 0.098386 | 0.78945 | 0.023846 |  | 0.0237 | 5.934e-09 | 0.39363 | 41607.1824 | 0.78209 | 0.94415 | 0.00014559 | 0.27018 | 8.5725e-07 | 0.45444 | 42920.7376 | 0.29673 | 0.90641 | 0.023704 |  | 0.047695
0.85039 | 1.2846e-06 | 0.51171 | 17603.8444 | 0.37239 | 0.85278 | 0.026209 |  | 0.9287 | 2.0031e-07 | 0.56865 | 45459.9778 | 0.51818 | 0.91717 | 0.0056294 | 0.58521 | 1.3362e-06 | 0.038327 | 30819.7737 | 0.37376 | 0.91638 | 0.028657 |  | 0.060495
0.50663 | 6.4673e-07 | 0.15324 | 14263.7219 | 0.70203 | 0.89879 | 0.0098795 |  | 0.86793 | 1.6017e-07 | 0.51389 | 44221.4078 | 0.4101 | 0.9054 | 0.0045338 | 0.42839 | 1.0892e-06 | 0.71718 | 49261.3234 | 0.36895 | 0.9158 | 0.032603 |  | 0.047017
0.72649 | 9.7739e-07 | 0.25476 | 15337.9177 | 0.53671 | 0.87648 | 0.017145 |  | 0.60386 | 8.4784e-08 | 0.97999 | 66218.1449 | 0.055478 | 0.83258 | 0.0035806 | 0.38485 | 1.0252e-06 | 0.36409 | 40965.7308 | 0.64359 | 0.94423 | 0.024837 |  | 0.045563
0.1948 | 3.0821e-07 | 0.98445 | 26934.4753 | 0.52632 | 0.87507 | 0.0070052 |  | 0.70317 | 1.0534e-07 | 0.77021 | 50914.7487 | 0.9944 | 0.98339 | 0.0027903 | 0.030263 | 3.7778e-07 | 0.89417 | 56375.9429 | 0.59957 | 0.94005 | 0.011995 |  | 0.02179
0.3728 | 4.9427e-07 | 0.19736 | 14761.5362 | 0.45562 | 0.86522 | 0.0089922 |  | 0.85824 | 1.5549e-07 | 0.95262 | 61338.9412 | 0.474 | 0.9125 | 0.0055434 | 0.13787 | 6.4321e-07 | 0.56514 | 45379.0173 | 0.42846 | 0.92267 | 0.017823 |  | 0.032358
0.71566 | 9.568e-07 | 0.21847 | 14980.781 | 0.76236 | 0.90735 | 0.014268 |  | 0.12548 | 1.9818e-08 | 0.8523 | 54136.8237 | 0.096972 | 0.85018 | 0.00071616 | 0.39779 | 1.0442e-06 | 0.27018 | 38853.2156 | 0.9976 | 0.99301 | 0.020782 |  | 0.035767
0.089155 | 1.8894e-07 | 0.84321 | 21408.5101 | 0.41176 | 0.85881 | 0.0040737 |  | 0.78568 | 1.2778e-07 | 0.081532 | 33224.1231 | 0.16609 | 0.86864 | 0.0033142 | 0.24922 | 8.2574e-07 | 0.69579 | 48652.7887 | 0.040499 | 0.83693 | 0.028607 |  | 0.035995
0.88826 | 1.4268e-06 | 0.25207 | 15312.1407 | 0.61099 | 0.88647 | 0.023874 |  | 0.95056 | 2.2375e-07 | 0.43378 | 42474.0985 | 0.60737 | 0.92623 | 0.005847 | 0.056557 | 4.647e-07 | 0.80136 | 52015.4792 | 0.62956 | 0.9429 | 0.01372 |  | 0.04344
0.3678 | 4.8891e-07 | 0.80417 | 20771.2135 | 0.8558 | 0.92228 | 0.0080114 |  | 0.58623 | 8.1611e-08 | 0.64375 | 47273.2272 | 0.26229 | 0.886 | 0.0025241 | 0.23278 | 8.0061e-07 | 0.61185 | 46482.3431 | 0.32143 | 0.90978 | 0.023256 |  | 0.033791
0.73653 | 9.9711e-07 | 0.49612 | 17466.7656 | 0.028721 | 0.74406 | 0.028835 |  | 0.735 | 1.1323e-07 | 0.67963 | 48210.6468 | 0.62119 | 0.92762 | 0.0032498 | 0.060586 | 4.7582e-07 | 0.11789 | 34643.9074 | 0.98539 | 0.9865 | 0.0086937 |  | 0.040778
0.35267 | 4.7278e-07 | 0.5347 | 17808.2952 | 0.61851 | 0.88748 | 0.0083963 |  | 0.87574 | 1.6419e-07 | 0.34913 | 40638.1949 | 0.28553 | 0.88946 | 0.0045572 | 0.96806 | 2.7445e-06 | 0.42324 | 42246.4695 | 0.11108 | 0.86954 | 0.081774 |  | 0.094728
0.010178 | 5.7056e-08 | 0.89269 | 22430.7655 | 0.41895 | 0.85988 | 0.0012506 |  | 0.13144 | 2.0539e-08 | 0.69374 | 48595.8878 | 0.87158 | 0.95481 | 0.00055781 | 0.22768 | 7.9273e-07 | 0.20235 | 37173.429 | 0.71627 | 0.95112 | 0.017408 |  | 0.019217
0.21703 | 3.3154e-07 | 0.65123 | 18915.391 | 0.28033 | 0.83709 | 0.0073561 |  | 0.19185 | 2.7726e-08 | 0.10481 | 34169.1582 | 0.85073 | 0.95212 | 0.00056729 | 0.95333 | 2.5625e-06 | 0.72432 | 49471.1877 | 0.47667 | 0.92784 | 0.07501 |  | 0.082933
0.29738 | 4.1484e-07 | 0.75461 | 20086.673 | 0.84689 | 0.92071 | 0.0067173 |  | 0.15379 | 2.3219e-08 | 0.76176 | 50634.7751 | 0.78047 | 0.94397 | 0.00066888 | 0.56547 | 1.3029e-06 | 0.0086994 | 27292.4565 | 0.19795 | 0.89035 | 0.028345 |  | 0.035731
0.76272 | 1.0517e-06 | 0.74858 | 20010.3021 | 0.21632 | 0.82408 | 0.024879 |  | 0.50232 | 6.7875e-08 | 0.091038 | 33628.2555 | 0.053407 | 0.83142 | 0.0019512 | 0.22304 | 7.8553e-07 | 0.27042 | 38858.8278 | 0.5059 | 0.93085 | 0.018965 |  | 0.045796
0.8137 | 1.1753e-06 | 0.36587 | 16341.0474 | 0.44482 | 0.86367 | 0.022329 |  | 0.12344 | 1.9569e-08 | 0.19688 | 37028.3222 | 0.30504 | 0.89222 | 0.00050803 | 0.68754 | 1.5272e-06 | 0.39848 | 41711.8601 | 0.90962 | 0.97192 | 0.034713 |  | 0.057551
0.29964 | 4.1719e-07 | 0.55158 | 17960.4789 | 0.86749 | 0.92441 | 0.0062257 |  | 0.82225 | 1.4041e-07 | 0.7237 | 49452.9049 | 0.60671 | 0.92617 | 0.0041237 | 0.9501 | 2.5299e-06 | 0.56734 | 45429.5994 | 0.41499 | 0.92117 | 0.070407 |  | 0.080756
0.93738 | 1.7009e-06 | 0.69672 | 19399.4528 | 0.62999 | 0.88901 | 0.031204 |  | 0.23774 | 3.3147e-08 | 0.048269 | 31496.3209 | 0.167 | 0.86884 | 0.00083439 | 0.41129 | 1.064e-06 | 0.22507 | 37758.296 | 0.34054 | 0.91227 | 0.026502 |  | 0.05854
0.74031 | 1.0047e-06 | 0.89124 | 22395.9024 | 0.13602 | 0.80297 | 0.026375 |  | 0.54682 | 7.4905e-08 | 0.90037 | 56768.3463 | 0.057991 | 0.83393 | 0.0028627 | 0.095042 | 5.5849e-07 | 0.64551 | 47317.8785 | 0.44582 | 0.92457 | 0.015907 |  | 0.045144
0.15733 | 2.6803e-07 | 0.93283 | 23610.2404 | 0.67079 | 0.89451 | 0.005307 |  | 0.53873 | 7.3587e-08 | 0.3306 | 40229.1509 | 0.60972 | 0.92647 | 0.0018453 | 0.24989 | 8.2675e-07 | 0.9673 | 63481.9831 | 0.52756 | 0.93303 | 0.029335 |  | 0.036487
0.79367 | 1.1235e-06 | 0.65233 | 18926.6461 | 0.72534 | 0.90204 | 0.019233 |  | 0.19509 | 2.8107e-08 | 0.44598 | 42737.5342 | 0.96189 | 0.97036 | 0.0006558 | 0.9934 | 3.4592e-06 | 0.24267 | 38194.6468 | 0.12141 | 0.87261 | 0.096248 |  | 0.11614
0.2542 | 3.7013e-07 | 0.5781 | 18204.1491 | 0.80149 | 0.91326 | 0.005889 |  | 0.48974 | 6.5976e-08 | 0.11325 | 34479.4982 | 0.56575 | 0.92204 | 0.0014993 | 0.17538 | 7.0876e-07 | 0.56609 | 45400.7529 | 0.90593 | 0.97143 | 0.017404 |  | 0.024792
0.74543 | 1.0151e-06 | 0.63588 | 18760.2195 | 0.95383 | 0.94488 | 0.013898 |  | 0.024697 | 6.1064e-09 | 0.086712 | 33447.8463 | 0.4768 | 0.9128 | 0.00013986 | 0.8665 | 2.0251e-06 | 0.65231 | 47491.8383 | 0.020619 | 0.81692 | 0.071764 |  | 0.085802
0.92841 | 1.6383e-06 | 0.006237 | 10618.0513 | 0.45744 | 0.86548 | 0.026834 |  | 0.00042202 | 3.8931e-10 | 0.55147 | 45065.5252 | 0.15393 | 0.86592 | 1.2169e-05 | 0.58343 | 1.3332e-06 | 0.45146 | 42856.178 | 0.73705 | 0.95312 | 0.032703 |  | 0.059549
0.1029 | 2.0588e-07 | 0.068356 | 12995.6649 | 0.76048 | 0.90707 | 0.0028894 |  | 0.72159 | 1.098e-07 | 0.81812 | 52661.875 | 0.21018 | 0.87734 | 0.0037164 | 0.16265 | 6.8715e-07 | 0.69786 | 48710.4829 | 0.43924 | 0.92385 | 0.020045 |  | 0.026651
0.70328 | 9.3406e-07 | 0.065002 | 12928.4087 | 0.051763 | 0.76479 | 0.023864 |  | 0.49366 | 6.6564e-08 | 0.16064 | 36013.046 | 0.20139 | 0.87573 | 0.0017743 | 0.13551 | 6.3886e-07 | 0.01187 | 27937.8594 | 0.026126 | 0.8238 | 0.017212 |  | 0.04285
0.27572 | 3.9239e-07 | 0.90231 | 22673.7211 | 0.49655 | 0.87098 | 0.0083096 |  | 0.9933 | 3.4842e-07 | 0.68373 | 48321.4575 | 0.25951 | 0.88557 | 0.010948 | 0.28097 | 8.7331e-07 | 0.76873 | 50865.1193 | 0.25774 | 0.90064 | 0.027605 |  | 0.046862
0.62689 | 8.0877e-07 | 0.77176 | 20311.2424 | 0.30583 | 0.84172 | 0.018128 |  | 0.69223 | 1.028e-07 | 0.23539 | 38015.8848 | 0.98933 | 0.97997 | 0.0020952 | 0.99439 | 3.5304e-06 | 0.5326 | 44638.9982 | 0.24062 | 0.8979 | 0.10233 |  | 0.12255
0.92267 | 1.6021e-06 | 0.6269 | 18671.1023 | 0.82303 | 0.9167 | 0.025401 |  | 0.99614 | 3.8221e-07 | 0.20736 | 37304.7714 | 0.44385 | 0.90921 | 0.0095215 | 0.019354 | 3.2809e-07 | 0.45588 | 42951.886 | 0.21744 | 0.89394 | 0.009347 |  | 0.04427
0.15976 | 2.7068e-07 | 0.15854 | 14327.1069 | 0.25196 | 0.83161 | 0.0056054 |  | 0.75498 | 1.1863e-07 | 0.19472 | 36970.4233 | 0.46974 | 0.91204 | 0.0029141 | 0.45261 | 1.1254e-06 | 0.019088 | 29010.3197 | 0.77982 | 0.95731 | 0.019835 |  | 0.028355
0.99714 | 3.068e-06 | 0.95385 | 24506.3386 | 0.22411 | 0.8258 | 0.077863 |  | 0.10004 | 1.6683e-08 | 0.28984 | 39309.704 | 0.5799 | 0.92347 | 0.00041465 | 0.81437 | 1.8417e-06 | 0.89714 | 56561.3702 | 0.15594 | 0.88151 | 0.065029 |  | 0.14331
0.97321 | 2.089e-06 | 0.89021 | 22371.0686 | 0.7554 | 0.90633 | 0.038319 |  | 0.75234 | 1.179e-07 | 0.082982 | 33287.6467 | 0.31247 | 0.89323 | 0.0028554 | 0.26676 | 8.5215e-07 | 0.41835 | 42141.0499 | 0.56234 | 0.93645 | 0.021558 |  | 0.062732
0.78222 | 1.0959e-06 | 0.56412 | 18074.9572 | 0.23982 | 0.82913 | 0.024616 |  | 0.41216 | 5.4975e-08 | 0.16329 | 36090.9962 | 0.68979 | 0.9345 | 0.0012425 | 0.91634 | 2.2714e-06 | 0.49075 | 43711.4153 | 0.85418 | 0.96513 | 0.054849 |  | 0.080708
0.042774 | 1.2387e-07 | 0.43114 | 16903.9729 | 0.40819 | 0.85828 | 0.0024363 |  | 0.48613 | 6.5439e-08 | 0.5796 | 45714.718 | 0.032281 | 0.81662 | 0.0022727 | 0.21062 | 7.6604e-07 | 0.094818 | 33781.5167 | 0.80972 | 0.96035 | 0.015087 |  | 0.019796
0.82945 | 1.2196e-06 | 0.88644 | 22282.5405 | 0.43802 | 0.86268 | 0.026392 |  | 0.92455 | 1.9666e-07 | 0.66942 | 47938.0603 | 0.37656 | 0.90144 | 0.0059471 | 0.80592 | 1.8161e-06 | 0.92562 | 58617.6196 | 0.27916 | 0.90388 | 0.063404 |  | 0.095743
0.0032066 | 3.1317e-08 | 0.69746 | 19407.6729 | 0.5897 | 0.88362 | 0.00058781 |  | 0.95938 | 2.3622e-07 | 0.022856 | 29448.3208 | 0.85967 | 0.95325 | 0.0042828 | 0.073858 | 5.0993e-07 | 0.18274 | 36644.0956 | 0.90045 | 0.9707 | 0.010378 |  | 0.015249
0.3915 | 5.1447e-07 | 0.5975 | 18386.5711 | 0.74921 | 0.90544 | 0.0085442 |  | 0.29298 | 3.9774e-08 | 0.40594 | 41873.136 | 0.054563 | 0.83207 | 0.001278 | 0.24604 | 8.209e-07 | 0.64778 | 47375.8869 | 0.86829 | 0.96675 | 0.02119 |  | 0.031012
0.53921 | 6.8755e-07 | 0.78692 | 20520.0786 | 0.51005 | 0.87284 | 0.013816 |  | 0.1212 | 1.9296e-08 | 0.26932 | 38832.9962 | 0.86913 | 0.95448 | 0.00043455 | 0.17292 | 7.0464e-07 | 0.59786 | 46145.8849 | 0.98994 | 0.98825 | 0.016792 |  | 0.031043
0.0352 | 1.1115e-07 | 0.44475 | 17021.1666 | 0.57855 | 0.88212 | 0.0019823 |  | 0.40322 | 5.3774e-08 | 0.84943 | 54003.224 | 0.83875 | 0.95065 | 0.0016128 | 0.38742 | 1.029e-06 | 0.23504 | 38007.1202 | 0.41187 | 0.92082 | 0.025144 |  | 0.028739
0.35101 | 4.7102e-07 | 0.17628 | 14531.5222 | 0.6106 | 0.88642 | 0.0077203 |  | 0.81326 | 1.3709e-07 | 0.88991 | 56118.1461 | 0.095194 | 0.84957 | 0.0050746 | 0.68591 | 1.5239e-06 | 0.73312 | 49734.5978 | 0.24602 | 0.89878 | 0.047571 |  | 0.060366
0.012765 | 6.4297e-08 | 0.49974 | 17498.4501 | 0.90775 | 0.93257 | 0.00090443 |  | 0.19509 | 2.8107e-08 | 0.31844 | 39958.0475 | 0.47754 | 0.91288 | 0.00072713 | 0.22901 | 7.948e-07 | 0.64961 | 47422.5887 | 0.41695 | 0.92139 | 0.022837 |  | 0.024469
0.22229 | 3.3703e-07 | 0.3564 | 16258.6139 | 0.22241 | 0.82543 | 0.0074156 |  | 0.1883 | 2.7306e-08 | 0.42637 | 42314.0794 | 0.96609 | 0.97145 | 0.00062952 | 0.055911 | 4.6287e-07 | 0.27444 | 38953.0907 | 0.79701 | 0.95904 | 0.010307 |  | 0.018352
0.19719 | 3.1074e-07 | 0.52991 | 17765.408 | 0.94742 | 0.94283 | 0.0041586 |  | 0.35123 | 4.7004e-08 | 0.43872 | 42580.6611 | 0.78231 | 0.94417 | 0.0011747 | 0.87084 | 2.043e-06 | 0.53282 | 44643.8672 | 0.13988 | 0.8776 | 0.061928 |  | 0.067261
0.97648 | 2.1474e-06 | 0.86787 | 21878.8451 | 0.85749 | 0.92259 | 0.036235 |  | 0.77021 | 1.2303e-07 | 0.29473 | 39421.9066 | 0.37164 | 0.90084 | 0.0032532 | 0.48841 | 1.1797e-06 | 0.4954 | 43813.2703 | 0.39623 | 0.91903 | 0.03212 |  | 0.071608
0.89965 | 1.4784e-06 | 0.78144 | 20443.2891 | 0.69225 | 0.89744 | 0.026844 |  | 0.97772 | 2.7401e-07 | 0.69793 | 48712.4842 | 0.92961 | 0.96362 | 0.0073043 | 0.94393 | 2.4727e-06 | 0.81378 | 52490.4214 | 0.30204 | 0.90715 | 0.078982 |  | 0.11313
0.79166 | 1.1186e-06 | 0.59268 | 18340.9241 | 0.92877 | 0.9376 | 0.015733 |  | 0.044093 | 9.1794e-09 | 0.41454 | 42058.7183 | 0.33464 | 0.89618 | 0.00025648 | 0.93761 | 2.4196e-06 | 0.028221 | 29985.7859 | 0.58555 | 0.9387 | 0.047047 |  | 0.063036
0.5698 | 7.2774e-07 | 0.53154 | 17779.9858 | 0.84345 | 0.92012 | 0.011045 |  | 0.13575 | 2.106e-08 | 0.42664 | 42319.9166 | 0.81313 | 0.94762 | 0.00051891 | 0.20453 | 7.5636e-07 | 0.21469 | 37494.5762 | 0.75316 | 0.95468 | 0.01654 |  | 0.028104
0.81743 | 1.1854e-06 | 0.58634 | 18281.2343 | 0.033195 | 0.74901 | 0.03418 |  | 0.71984 | 1.0937e-07 | 0.28198 | 39128.4817 | 0.82135 | 0.94858 | 0.0025224 | 0.30479 | 9.0844e-07 | 0.42177 | 42214.8424 | 0.7443 | 0.95382 | 0.021964 |  | 0.058666
0.21068 | 3.2491e-07 | 0.68591 | 19280.7058 | 0.25381 | 0.83198 | 0.0073882 |  | 0.8773 | 1.6502e-07 | 0.5505 | 45043.6532 | 0.8537 | 0.95249 | 0.0042267 | 0.91647 | 2.2722e-06 | 0.62614 | 46832.3192 | 0.44989 | 0.92501 | 0.064143 |  | 0.075758
0.3461 | 4.6583e-07 | 0.78464 | 20488.0076 | 0.40261 | 0.85744 | 0.0099092 |  | 0.52307 | 7.1089e-08 | 0.94824 | 60816.1505 | 0.474 | 0.9125 | 0.0025174 | 0.3339 | 9.5099e-07 | 0.26665 | 38770.1089 | 0.0054812 | 0.78055 | 0.032671 |  | 0.045098
0.17233 | 2.8428e-07 | 0.16268 | 14375.7385 | 0.39518 | 0.85631 | 0.0053281 |  | 0.15649 | 2.3541e-08 | 0.84981 | 54020.7085 | 0.43917 | 0.90869 | 0.00076608 | 0.86004 | 1.9994e-06 | 0.92495 | 58561.8341 | 0.65405 | 0.94522 | 0.064932 |  | 0.071026
0.60037 | 7.7005e-07 | 0.38172 | 16478.4205 | 0.90228 | 0.93136 | 0.010539 |  | 0.47614 | 6.3965e-08 | 0.088356 | 33517.0932 | 0.97141 | 0.97296 | 0.0011945 | 0.027244 | 3.653e-07 | 0.0272 | 29889.7986 | 0.13138 | 0.87538 | 0.0087669 |  | 0.0205
0.21595 | 3.3041e-07 | 0.70386 | 19479.2793 | 0.18223 | 0.816 | 0.0079518 |  | 0.99615 | 3.8238e-07 | 0.46261 | 43097.8271 | 0.90778 | 0.95999 | 0.0092502 | 0.2899 | 8.8653e-07 | 0.11032 | 34373.4412 | 0.28954 | 0.90539 | 0.021143 |  | 0.038345
0.90442 | 1.5017e-06 | 0.015208 | 11351.1372 | 0.033068 | 0.74888 | 0.039417 |  | 0.11232 | 1.8208e-08 | 0.71321 | 49146.4461 | 0.12624 | 0.85901 | 0.00060924 | 0.061866 | 4.7927e-07 | 0.73029 | 49649.1017 | 0.90599 | 0.97143 | 0.012757 |  | 0.052783
0.64278 | 8.3301e-07 | 0.50666 | 17559.2594 | 0.4284 | 0.86128 | 0.016422 |  | 0.34331 | 4.6002e-08 | 0.56112 | 45286.3989 | 0.25655 | 0.88511 | 0.0013849 | 0.79818 | 1.7935e-06 | 0.92367 | 58456.942 | 0.052982 | 0.84526 | 0.068622 |  | 0.086428
0.42228 | 5.4837e-07 | 0.55699 | 18009.7853 | 0.67572 | 0.89518 | 0.0094555 |  | 0.041148 | 8.7395e-09 | 0.33206 | 40261.6691 | 0.84852 | 0.95184 | 0.00020433 | 0.6689 | 1.4896e-06 | 0.85918 | 54465.6973 | 0.45304 | 0.92535 | 0.047279 |  | 0.056939
0.98783 | 2.4399e-06 | 0.77777 | 20392.83 | 0.70133 | 0.89869 | 0.04401 |  | 0.11825 | 1.8936e-08 | 0.65416 | 47539.3681 | 0.83908 | 0.95069 | 0.00050971 | 0.7877 | 1.764e-06 | 0.16378 | 36105.243 | 0.033781 | 0.83144 | 0.052524 |  | 0.097044
0.48378 | 6.1915e-07 | 0.21028 | 14896.9406 | 0.079553 | 0.78101 | 0.015479 |  | 0.04084 | 8.6931e-09 | 0.77673 | 51135.7141 | 0.22622 | 0.88016 | 0.00028689 | 0.17594 | 7.097e-07 | 0.41653 | 42101.7028 | 0.49771 | 0.93002 | 0.018245 |  | 0.034011
0.90104 | 1.4851e-06 | 0.86545 | 21829.801 | 0.68175 | 0.896 | 0.028053 |  | 0.59881 | 8.3863e-08 | 0.9428 | 60218.9141 | 0.63165 | 0.92866 | 0.002869 | 0.34346 | 9.6492e-07 | 0.75095 | 50286.8647 | 0.49858 | 0.93011 | 0.028473 |  | 0.059396
0.3028 | 4.2047e-07 | 0.08675 | 13330.2498 | 0.0064229 | 0.69701 | 0.013114 |  | 0.50819 | 6.8774e-08 | 0.5143 | 44230.5558 | 0.12015 | 0.85733 | 0.0021635 | 0.52476 | 1.2366e-06 | 0.52585 | 44487.7272 | 0.061681 | 0.85007 | 0.039624 |  | 0.054901
0.015016 | 7.0085e-08 | 0.37993 | 16462.9386 | 0.77532 | 0.90927 | 0.0010816 |  | 0.95508 | 2.2984e-07 | 0.39295 | 41592.276 | 0.30999 | 0.89289 | 0.0064244 | 0.73931 | 1.6409e-06 | 0.74413 | 50072.405 | 0.20735 | 0.89211 | 0.052159 |  | 0.059665
0.63107 | 8.1507e-07 | 0.83715 | 21302.2046 | 0.60788 | 0.88605 | 0.015828 |  | 0.10712 | 1.7565e-08 | 0.63591 | 47075.4619 | 0.15048 | 0.86512 | 0.00056521 | 0.10816 | 5.8596e-07 | 0.12457 | 34874.49 | 0.94563 | 0.97737 | 0.011148 |  | 0.027541
0.93558 | 1.6877e-06 | 0.27976 | 15572.9677 | 0.13732 | 0.80338 | 0.039626 |  | 0.30262 | 4.095e-08 | 0.81227 | 52431.3722 | 0.43508 | 0.90824 | 0.0013042 | 0.45252 | 1.1252e-06 | 0.33612 | 40351.6142 | 0.44517 | 0.9245 | 0.02843 |  | 0.06936
0.16416 | 2.7546e-07 | 0.83991 | 21350.2981 | 0.14623 | 0.80611 | 0.007049 |  | 0.45087 | 6.0325e-08 | 0.42928 | 42376.9834 | 0.87707 | 0.95555 | 0.0014563 | 0.86002 | 1.9993e-06 | 0.66827 | 47907.4253 | 0.60701 | 0.94076 | 0.05543 |  | 0.063935
0.24031 | 3.5574e-07 | 0.77226 | 20318.026 | 0.39285 | 0.85595 | 0.0075823 |  | 0.79989 | 1.3243e-07 | 0.64294 | 47252.8434 | 0.077951 | 0.84314 | 0.0044578 | 0.96806 | 2.7445e-06 | 0.35443 | 40754.479 | 0.51369 | 0.93164 | 0.068538 |  | 0.080578
0.4522 | 5.8224e-07 | 0.37329 | 16405.4842 | 0.92626 | 0.93696 | 0.0076903 |  | 0.33242 | 4.4635e-08 | 0.85708 | 54364.0131 | 0.15395 | 0.86592 | 0.0015748 | 0.97107 | 2.7911e-06 | 0.77448 | 51059.0526 | 0.024341 | 0.82173 | 0.10214 |  | 0.11141
0.36295 | 4.8373e-07 | 0.74128 | 19919.5794 | 0.36977 | 0.85237 | 0.010362 |  | 0.99229 | 3.3979e-07 | 0.35223 | 40706.3642 | 0.3363 | 0.8964 | 0.009283 | 0.3748 | 1.0106e-06 | 0.84204 | 53668.3303 | 0.34997 | 0.91346 | 0.032432 |  | 0.052077
0.58008 | 7.4172e-07 | 0.43403 | 16928.8765 | 0.59133 | 0.88384 | 0.013097 |  | 0.79961 | 1.3233e-07 | 0.021607 | 29309.6368 | 0.45064 | 0.90996 | 0.0028085 | 0.5791 | 1.3258e-06 | 0.63589 | 47075.1918 | 0.79374 | 0.95871 | 0.034713 |  | 0.050618
0.07192 | 1.6653e-07 | 0.1086 | 13673.2091 | 0.62551 | 0.88841 | 0.0026393 |  | 0.5604 | 7.716e-08 | 0.94688 | 60662.0713 | 0.86555 | 0.95401 | 0.0025435 | 0.32312 | 9.3526e-07 | 0.793 | 51708.4951 | 0.73253 | 0.95268 | 0.026913 |  | 0.032096
0.28785 | 4.0495e-07 | 0.37036 | 16380.019 | 0.3956 | 0.85637 | 0.0079352 |  | 0.43967 | 5.8751e-08 | 0.33442 | 40313.9174 | 0.60982 | 0.92648 | 0.0014756 | 0.80336 | 1.8086e-06 | 0.52376 | 44441.1167 | 0.41755 | 0.92146 | 0.049475 |  | 0.058885
0.52763 | 6.7283e-07 | 0.055911 | 12733.4635 | 0.19351 | 0.81879 | 0.014188 |  | 0.10963 | 1.7876e-08 | 0.62578 | 46823.5458 | 0.55073 | 0.92052 | 0.00050972 | 0.3252 | 9.3831e-07 | 0.13819 | 35323.5896 | 0.27487 | 0.90325 | 0.022921 |  | 0.037619
0.67068 | 8.7773e-07 | 0.86589 | 21838.4998 | 0.98788 | 0.96123 | 0.012193 |  | 0.098125 | 1.6442e-08 | 0.29311 | 39384.8108 | 0.20532 | 0.87646 | 0.00046172 | 0.455 | 1.1289e-06 | 0.28959 | 39303.9617 | 0.96581 | 0.98124 | 0.023625 |  | 0.03628
0.70416 | 9.3565e-07 | 0.34895 | 16193.5735 | 0.37012 | 0.85242 | 0.018554 |  | 0.14833 | 2.2568e-08 | 0.8838 | 55761.6923 | 0.10662 | 0.85331 | 0.0008269 | 0.59361 | 1.3507e-06 | 0.39261 | 41584.9826 | 0.10623 | 0.86801 | 0.039994 |  | 0.059375
0.87358 | 1.367e-06 | 0.0344 | 12161.7786 | 0.34248 | 0.84796 | 0.025256 |  | 0.44406 | 5.9365e-08 | 0.051395 | 31688.3536 | 0.91994 | 0.96195 | 0.0011027 | 0.93587 | 2.4059e-06 | 0.37256 | 41150.2819 | 0.22008 | 0.89441 | 0.066529 |  | 0.092887
0.13793 | 2.4656e-07 | 0.28596 | 15630.1508 | 0.45854 | 0.86564 | 0.0045701 |  | 0.66571 | 9.6962e-08 | 0.68392 | 48326.5278 | 0.49011 | 0.91422 | 0.0028705 | 0.64629 | 1.4459e-06 | 0.74543 | 50113.1432 | 0.62627 | 0.94259 | 0.04142 |  | 0.048861
0.39079 | 5.137e-07 | 0.080432 | 13221.0555 | 0.43619 | 0.86242 | 0.0091199 |  | 0.70972 | 1.0689e-07 | 0.231 | 37906.7958 | 0.73581 | 0.93922 | 0.002472 | 0.67146 | 1.4947e-06 | 0.46723 | 43198.2318 | 0.72755 | 0.9522 | 0.036999 |  | 0.04859
0.50586 | 6.4578e-07 | 0.5595 | 18032.6685 | 0.70393 | 0.89905 | 0.010946 |  | 0.93132 | 2.0271e-07 | 0.16136 | 36034.0373 | 0.97347 | 0.97358 | 0.0040249 | 0.70247 | 1.5585e-06 | 0.28336 | 39160.499 | 0.70261 | 0.94982 | 0.035835 |  | 0.050805
0.79667 | 1.131e-06 | 0.51986 | 17675.9389 | 0.29551 | 0.83988 | 0.02426 |  | 0.84231 | 1.4842e-07 | 0.25459 | 38483.1498 | 0.29807 | 0.89124 | 0.0039591 | 0.58618 | 1.3379e-06 | 0.29506 | 39429.4332 | 0.97902 | 0.9845 | 0.027784 |  | 0.056002
0.24003 | 3.5546e-07 | 0.52037 | 17680.5087 | 0.29695 | 0.84013 | 0.0076178 |  | 0.45959 | 6.1566e-08 | 0.97653 | 65340.0983 | 0.90087 | 0.95894 | 0.0021502 | 0.60515 | 1.3708e-06 | 0.22372 | 37724.3574 | 0.65661 | 0.94546 | 0.030996 |  | 0.040764
0.25241 | 3.6828e-07 | 0.38247 | 16484.8674 | 0.80784 | 0.91426 | 0.0055414 |  | 0.55695 | 7.6582e-08 | 0.028455 | 30007.4207 | 0.92924 | 0.96356 | 0.0013516 | 0.56568 | 1.3032e-06 | 0.017102 | 28752.2045 | 0.88854 | 0.96919 | 0.021675 |  | 0.028568
0.52247 | 6.6634e-07 | 0.82911 | 21165.6437 | 0.14633 | 0.80614 | 0.017 |  | 0.23849 | 3.3235e-08 | 0.72118 | 49378.6005 | 0.96652 | 0.97156 | 0.00088002 | 0.7071 | 1.5684e-06 | 0.6369 | 47100.3691 | 0.48446 | 0.92865 | 0.044104 |  | 0.061984
0.23352 | 3.487e-07 | 0.86485 | 21817.6481 | 0.69006 | 0.89714 | 0.0065546 |  | 0.19689 | 2.832e-08 | 0.28158 | 39119.3108 | 0.72482 | 0.93808 | 0.00067324 | 0.5048 | 1.2051e-06 | 0.27105 | 38873.5902 | 0.034826 | 0.83235 | 0.037196 |  | 0.044424
0.48934 | 6.2578e-07 | 0.4065 | 16692.0685 | 0.61579 | 0.88711 | 0.010822 |  | 0.88985 | 1.7209e-07 | 0.55193 | 45076.0221 | 0.80192 | 0.94635 | 0.0044794 | 0.62003 | 1.3974e-06 | 0.080241 | 33166.959 | 0.46515 | 0.92663 | 0.030454 |  | 0.045755
0.47386 | 6.0741e-07 | 0.53213 | 17785.2259 | 0.42218 | 0.86036 | 0.012077 |  | 0.61707 | 8.7241e-08 | 0.092612 | 33692.5637 | 0.81334 | 0.94765 | 0.0017929 | 0.71162 | 1.5782e-06 | 0.42845 | 42359.0827 | 0.5879 | 0.93893 | 0.039828 |  | 0.053698
0.43858 | 5.6669e-07 | 0.81651 | 20961.179 | 0.94647 | 0.94254 | 0.0084504 |  | 0.73294 | 1.1269e-07 | 0.70276 | 48848.217 | 0.92336 | 0.96253 | 0.0030191 | 0.83788 | 1.9182e-06 | 0.39805 | 41702.7566 | 0.80711 | 0.96008 | 0.045109 |  | 0.056579
0.9004 | 1.482e-06 | 0.48608 | 17379.0208 | 0.92358 | 0.93629 | 0.020329 |  | 0.96365 | 2.4324e-07 | 0.12225 | 34795.4402 | 0.50428 | 0.91572 | 0.0056711 | 0.87462 | 2.059e-06 | 0.13725 | 35293.2842 | 0.44141 | 0.92409 | 0.047269 |  | 0.073269
0.13022 | 2.3785e-07 | 0.97514 | 25912.7396 | 0.58781 | 0.88336 | 0.0051524 |  | 0.013905 | 4.1063e-09 | 0.88468 | 55811.7328 | 0.53413 | 0.91882 | 0.00013449 | 0.65637 | 1.4651e-06 | 0.98227 | 66878.3407 | 0.77921 | 0.95725 | 0.052385 |  | 0.057672
0.39488 | 5.1816e-07 | 0.36747 | 16354.9867 | 0.58248 | 0.88265 | 0.0090666 |  | 0.95345 | 2.2758e-07 | 0.61783 | 46627.9252 | 0.26011 | 0.88566 | 0.0069784 | 0.11803 | 6.0566e-07 | 0.30023 | 39547.273 | 0.002881 | 0.76399 | 0.021671 |  | 0.037716
0.13638 | 2.4482e-07 | 0.90024 | 22619.9583 | 0.75517 | 0.9063 | 0.0045189 |  | 0.83495 | 1.4537e-07 | 0.12335 | 34833.1147 | 0.51118 | 0.91644 | 0.0033845 | 0.2904 | 8.8727e-07 | 0.005076 | 26261.9877 | 0.39681 | 0.91909 | 0.016996 |  | 0.0249
0.37447 | 4.9606e-07 | 0.52162 | 17691.575 | 0.10046 | 0.7903 | 0.01258 |  | 0.92218 | 1.9467e-07 | 0.84093 | 53618.8359 | 0.57421 | 0.9229 | 0.0061314 | 0.60446 | 1.3696e-06 | 0.083641 | 33316.2778 | 0.42203 | 0.92196 | 0.030398 |  | 0.04911
0.93544 | 1.6867e-06 | 0.43829 | 16965.5437 | 0.24727 | 0.83066 | 0.036905 |  | 0.023884 | 5.9659e-09 | 0.0019099 | 24623.7129 | 0.083874 | 0.84547 | 0.00014286 | 0.22501 | 7.8859e-07 | 0.48466 | 43578.046 | 0.027999 | 0.82584 | 0.026221 |  | 0.063269
0.51099 | 6.5208e-07 | 0.38064 | 16469.0924 | 0.11926 | 0.79738 | 0.015856 |  | 0.63994 | 9.1671e-08 | 0.91618 | 57870.7103 | 0.80415 | 0.9466 | 0.0029397 | 0.97131 | 2.795e-06 | 0.88684 | 55936.7558 | 0.80299 | 0.95965 | 0.084897 |  | 0.10369
0.8203 | 1.1934e-06 | 0.5735 | 18161.5061 | 0.48062 | 0.86876 | 0.023135 |  | 0.33057 | 4.4403e-08 | 0.3806 | 41324.8271 | 0.023175 | 0.80728 | 0.0014903 | 0.83943 | 1.9236e-06 | 0.9429 | 60229.4545 | 0.97355 | 0.98304 | 0.059803 |  | 0.084428
0.90474 | 1.5033e-06 | 0.066736 | 12963.4589 | 0.056211 | 0.76782 | 0.038057 |  | 0.60656 | 8.5282e-08 | 0.22543 | 37767.6004 | 0.26948 | 0.88709 | 0.0022721 | 0.24423 | 8.1815e-07 | 0.95198 | 61259.6734 | 0.7102 | 0.95054 | 0.027365 |  | 0.067694
0.098337 | 2.0033e-07 | 0.93386 | 23648.0126 | 0.44795 | 0.86412 | 0.0044315 |  | 0.010541 | 3.3972e-09 | 0.44575 | 42732.7384 | 0.81465 | 0.9478 | 8.4331e-05 | 0.71671 | 1.5894e-06 | 0.36353 | 40953.5159 | 0.73073 | 0.95251 | 0.037613 |  | 0.042128
0.29074 | 4.0795e-07 | 0.15543 | 14289.9619 | 0.58781 | 0.88337 | 0.0067429 |  | 0.97978 | 2.8008e-07 | 0.95608 | 61782.2742 | 0.031859 | 0.81624 | 0.011571 | 0.57973 | 1.3269e-06 | 0.2632 | 38688.5298 | 0.65589 | 0.9454 | 0.030612 |  | 0.048926
0.56902 | 7.267e-07 | 0.993 | 28609.2394 | 0.06059 | 0.77061 | 0.022613 |  | 0.49116 | 6.6189e-08 | 0.87074 | 55049.033 | 0.66297 | 0.9318 | 0.002093 | 0.40269 | 1.0513e-06 | 0.90054 | 56779.0571 | 0.87977 | 0.96811 | 0.031832 |  | 0.056538
0.47806 | 6.1236e-07 | 0.81982 | 21013.7742 | 0.098643 | 0.78956 | 0.016369 |  | 0.8576 | 1.5519e-07 | 0.093718 | 33737.3267 | 0.15312 | 0.86573 | 0.0040917 | 0.97767 | 2.912e-06 | 0.28176 | 39123.3886 | 0.24889 | 0.89924 | 0.076928 |  | 0.097388
0.53638 | 6.8393e-07 | 0.09647 | 13488.7872 | 0.54436 | 0.87752 | 0.011386 |  | 0.074307 | 1.3379e-08 | 0.93583 | 59524.1006 | 0.66752 | 0.93226 | 0.0004506 | 0.15715 | 6.7764e-07 | 0.59581 | 46097.102 | 0.89611 | 0.97014 | 0.016925 |  | 0.028761
0.018868 | 7.918e-08 | 0.23628 | 15158.7866 | 0.030032 | 0.74558 | 0.0022122 |  | 0.15886 | 2.3822e-08 | 0.70704 | 48969.4885 | 0.61115 | 0.92661 | 0.00069363 | 0.71646 | 1.5889e-06 | 0.79822 | 51899.1917 | 0.48975 | 0.9292 | 0.048165 |  | 0.051071
0.58395 | 7.4704e-07 | 0.60108 | 18420.7045 | 0.18761 | 0.81734 | 0.017577 |  | 0.96153 | 2.3966e-07 | 0.83112 | 53194.8297 | 0.36877 | 0.90049 | 0.0078293 | 0.65554 | 1.4635e-06 | 0.92148 | 58280.3929 | 0.71149 | 0.95067 | 0.046868 |  | 0.072275
0.3866 | 5.0916e-07 | 0.26243 | 15410.7947 | 0.36964 | 0.85235 | 0.0099297 |  | 0.90488 | 1.8166e-07 | 0.48415 | 43566.7965 | 0.20478 | 0.87636 | 0.0054356 | 0.83253 | 1.9e-06 | 0.99673 | 75654.9555 | 0.1165 | 0.87118 | 0.084055 |  | 0.099421
0.65299 | 8.4904e-07 | 0.2466 | 15259.4469 | 0.27045 | 0.83522 | 0.017666 |  | 0.5287 | 7.1979e-08 | 0.022187 | 29374.8103 | 0.39224 | 0.90331 | 0.0015646 | 0.64791 | 1.449e-06 | 0.7454 | 50112.0478 | 0.10769 | 0.86847 | 0.048225 |  | 0.067455
0.47213 | 6.0537e-07 | 0.17539 | 14521.5281 | 0.63571 | 0.88978 | 0.009756 |  | 0.344 | 4.609e-08 | 0.34737 | 40599.5736 | 0.30428 | 0.89211 | 0.0012703 | 0.50718 | 1.2089e-06 | 0.97638 | 65305.4233 | 0.79284 | 0.95862 | 0.042222 |  | 0.053248
0.77428 | 1.0775e-06 | 0.33278 | 16051.3398 | 0.49335 | 0.87053 | 0.019749 |  | 0.64081 | 9.1845e-08 | 0.97072 | 64106.899 | 0.18189 | 0.87195 | 0.0035972 | 0.78907 | 1.7678e-06 | 0.84879 | 53973.5815 | 0.65166 | 0.945 | 0.053601 |  | 0.076947
0.84476 | 1.2663e-06 | 0.86914 | 21905.0085 | 0.49199 | 0.87034 | 0.026453 |  | 0.14347 | 2.1987e-08 | 0.10286 | 34095.1961 | 0.037839 | 0.8212 | 0.00065217 | 0.012526 | 2.8724e-07 | 0.091037 | 33628.198 | 0.035531 | 0.83296 | 0.0082261 |  | 0.035332
0.65598 | 8.538e-07 | 0.61351 | 18540.158 | 0.89095 | 0.92898 | 0.012665 |  | 0.78911 | 1.2887e-07 | 0.98148 | 66639.7287 | 0.73974 | 0.93963 | 0.0047163 | 0.40212 | 1.0505e-06 | 0.95508 | 61651.6941 | 0.91851 | 0.97316 | 0.033984 |  | 0.051365
0.47512 | 6.0889e-07 | 0.78271 | 20460.9294 | 0.91539 | 0.93431 | 0.0093237 |  | 0.93631 | 2.0756e-07 | 0.87213 | 55122.0815 | 0.80624 | 0.94684 | 0.006383 | 0.13874 | 6.448e-07 | 0.021757 | 29326.6005 | 0.042185 | 0.83818 | 0.017065 |  | 0.032772
0.85466 | 1.2988e-06 | 0.8627 | 21774.7477 | 0.76775 | 0.90814 | 0.023293 |  | 0.42506 | 5.673e-08 | 0.27215 | 38899.3674 | 0.14061 | 0.86274 | 0.0016341 | 0.22422 | 7.8736e-07 | 0.823 | 52858.4845 | 0.21796 | 0.89403 | 0.025913 |  | 0.05084
0.15317 | 2.6347e-07 | 0.98281 | 26718.7128 | 0.49617 | 0.87092 | 0.0060446 |  | 0.80583 | 1.3447e-07 | 0.089753 | 33575.2345 | 0.97465 | 0.97396 | 0.0025053 | 0.4811 | 1.1685e-06 | 0.61131 | 46469.1847 | 0.12919 | 0.87479 | 0.036568 |  | 0.045118
0.55909 | 7.1346e-07 | 0.59209 | 18335.3201 | 0.69576 | 0.89792 | 0.012253 |  | 0.40808 | 5.4425e-08 | 0.28619 | 39225.898 | 0.81899 | 0.9483 | 0.0012587 | 0.6957 | 1.5442e-06 | 0.89353 | 56336.7105 | 0.042428 | 0.83836 | 0.058331 |  | 0.071843
0.61136 | 7.8586e-07 | 0.74562 | 19973.3786 | 0.6783 | 0.89553 | 0.01422 |  | 0.79633 | 1.3124e-07 | 0.35255 | 40713.4243 | 0.18083 | 0.87173 | 0.0038035 | 0.32077 | 9.3184e-07 | 0.77324 | 51016.8693 | 0.88083 | 0.96824 | 0.025607 |  | 0.043631
0.79076 | 1.1164e-06 | 0.38988 | 16548.9112 | 0.32307 | 0.84471 | 0.02299 |  | 0.46479 | 6.2313e-08 | 0.61793 | 46630.4975 | 0.21234 | 0.87773 | 0.0019426 | 0.34937 | 9.7353e-07 | 0.42992 | 42390.6958 | 0.069496 | 0.85391 | 0.030079 |  | 0.055011
0.8511 | 1.2869e-06 | 0.68385 | 19258.3192 | 0.90188 | 0.93128 | 0.019287 |  | 0.37146 | 4.9598e-08 | 0.15016 | 35698.0878 | 0.98674 | 0.97864 | 0.00095919 | 0.64444 | 1.4424e-06 | 0.070476 | 32713.678 | 0.16967 | 0.88459 | 0.035453 |  | 0.055699
0.62668 | 8.0846e-07 | 0.1406 | 14107.633 | 0.39903 | 0.8569 | 0.015022 |  | 0.29727 | 4.0296e-08 | 0.3279 | 40169.2219 | 0.024614 | 0.80896 | 0.0013291 | 0.60244 | 1.3661e-06 | 0.099345 | 33960.1059 | 0.51584 | 0.93185 | 0.02977 |  | 0.046121
0.69075 | 9.1182e-07 | 0.80328 | 20757.9025 | 0.099846 | 0.79005 | 0.024247 |  | 0.75082 | 1.1747e-07 | 0.21819 | 37584.0913 | 0.62572 | 0.92807 | 0.002789 | 0.073691 | 5.0953e-07 | 0.79217 | 51678.292 | 0.044313 | 0.8397 | 0.01821 |  | 0.045246
0.20842 | 3.2254e-07 | 0.9033 | 22699.9632 | 0.57085 | 0.88109 | 0.0065852 |  | 0.73377 | 1.1291e-07 | 0.54733 | 44971.5411 | 0.92086 | 0.96211 | 0.0028174 | 0.30812 | 9.1332e-07 | 0.12137 | 34764.8698 | 0.744 | 0.95379 | 0.018839 |  | 0.028242
0.88815 | 1.4263e-06 | 0.55842 | 18022.8383 | 0.55953 | 0.87957 | 0.026353 |  | 0.73751 | 1.1388e-07 | 0.57917 | 45704.6056 | 0.069664 | 0.8396 | 0.0037853 | 0.91896 | 2.2876e-06 | 0.47008 | 43260.1292 | 0.70432 | 0.94998 | 0.05703 |  | 0.087168
0.50073 | 6.3953e-07 | 0.16625 | 14417.304 | 0.13473 | 0.80256 | 0.014761 |  | 0.25963 | 3.5754e-08 | 0.53214 | 44628.6377 | 0.68306 | 0.93382 | 0.00095229 | 0.75742 | 1.6847e-06 | 0.39425 | 41620.4945 | 0.037357 | 0.83447 | 0.053685 |  | 0.069398
0.7132 | 9.5222e-07 | 0.34607 | 16168.2882 | 0.62741 | 0.88867 | 0.016128 |  | 0.26284 | 3.6137e-08 | 0.34296 | 40502.6316 | 0.26372 | 0.88622 | 0.0010088 | 0.13108 | 6.3063e-07 | 0.49235 | 43746.3974 | 0.49563 | 0.9298 | 0.016704 |  | 0.03384
0.87809 | 1.3847e-06 | 0.97232 | 25673.1561 | 0.36684 | 0.8519 | 0.033106 |  | 0.11718 | 1.8805e-08 | 0.98003 | 66228.0861 | 0.98118 | 0.97625 | 0.00064705 | 0.87844 | 2.0756e-06 | 0.62936 | 46912.2308 | 0.8082 | 0.96019 | 0.053987 |  | 0.08774
0.57967 | 7.4115e-07 | 0.0088241 | 10887.9994 | 0.016283 | 0.7254 | 0.020755 |  | 0.79805 | 1.3181e-07 | 0.20312 | 37193.7958 | 0.096888 | 0.85015 | 0.0038142 | 0.99065 | 3.3061e-06 | 0.39966 | 41737.5488 | 0.61771 | 0.94178 | 0.081839 |  | 0.10641
0.6298 | 8.1315e-07 | 0.42373 | 16840.2891 | 0.13663 | 0.80316 | 0.01952 |  | 0.88057 | 1.6679e-07 | 0.53015 | 44584.0043 | 0.69233 | 0.93476 | 0.0044288 | 0.16099 | 6.8431e-07 | 0.9992 | 82557.27 | 0.15549 | 0.8814 | 0.032007 |  | 0.055956
0.89799 | 1.4706e-06 | 0.75253 | 20060.2901 | 0.072666 | 0.7775 | 0.040132 |  | 0.3844 | 5.1283e-08 | 0.5797 | 45717.1005 | 0.93496 | 0.9646 | 0.0012898 | 0.877 | 2.0694e-06 | 0.81525 | 52547.9507 | 0.90635 | 0.97148 | 0.057989 |  | 0.099411
0.60724 | 7.7989e-07 | 0.94274 | 23995.9214 | 0.68452 | 0.89638 | 0.015467 |  | 0.32169 | 4.3299e-08 | 0.80227 | 52049.5623 | 0.91 | 0.96034 | 0.0012326 | 0.033432 | 3.9012e-07 | 0.32355 | 40072.3882 | 0.53851 | 0.93412 | 0.009553 |  | 0.026252
Note on B10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These are the point values at the specified confidence limit.
Note on G52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This uses the same calculation as B29 above, but it is repeated many times for different MC draws.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Dist Curves
This tab is only used for the data in the distribution charts. You may have to change the x-axis scale and values if your parameters change a lot.
You can also add the data to make new PDF graphs here.
Sensor |  | Logic solver |  | Final Element |  | Fitted System PFDavg |  | Sensor PT Interval
Lambda | Probability | Lambda | Probability | Lambda | Probability | PFDavg | Probability | PTI | Probability
1e-09 | 6888.2579 | 1e-10 | 826029.0636 | 1e-09 | 0.014683 | 0.0001 | 5.4818e-09 | 0.001 | 0
5e-09 | 34081.1387 | 5e-10 | 1834158.2119 | 5e-09 | 1.813 | 0.0003 | 6.0603e-07 | 5000 | 1.2035e-12
1e-08 | 67272.4838 | 1e-09 | 2571268.1645 | 1e-08 | 14.2831 | 0.0006 | 1.1608e-05 | 10000 | 3.9766e-06
5e-08 | 302798.9963 | 2e-09 | 3573168.7841 | 5e-08 | 1579.3196 | 0.001 | 0.00010057 | 12000 | 2.8038e-05
1e-07 | 531028.8691 | 3e-09 | 4300216.502 | 1e-07 | 10838.8365 | 0.00125 | 0.00025647 | 13000 | 5.0831e-05
2e-07 | 816611.5867 | 4e-09 | 4879225.0546 | 2e-07 | 63814.293 | 0.0015 | 0.00054872 | 13500 | 6.3654e-05
3e-07 | 941833.6587 | 5e-09 | 5360397.7672 | 3e-07 | 158502.8412 | 0.00175 | 0.00104 | 14000 | 7.6443e-05
4e-07 | 965562.4182 | 6e-09 | 5770039.7006 | 4e-07 | 276502.1885 | 0.002 | 0.001804 | 14500 | 8.8398e-05
5e-07 | 928020.9423 | 7e-09 | 6124115.274 | 5e-07 | 397442.1504 | 0.003 | 0.0093909 | 15000 | 9.8791e-05
6e-07 | 856261.5311 | 8e-09 | 6433250.9229 | 6e-07 | 505432.2786 | 0.004 | 0.029455 | 15500 | 0.00010704
7e-07 | 768105.072 | 9e-09 | 6704986.5789 | 7e-07 | 590675.088 | 0.005 | 0.069992 | 16000 | 0.00011275
8e-07 | 674963.0367 | 1e-08 | 6944929.1384 | 8e-07 | 648888.0967 | 0.006 | 0.13953 | 16500 | 0.00011576
9e-07 | 583848.1691 | 2e-08 | 8243173.1695 | 9e-07 | 679943.2811 | 0.007 | 0.24639 | 17000 | 0.00011611
1e-06 | 498798.1377 | 3e-08 | 8473281.9863 | 1e-06 | 686420.8555 | 0.008 | 0.39813 | 17500 | 0.00011398
1.1e-06 | 421876.0962 | 4e-08 | 8211691.6806 | 1.1e-06 | 672378.5302 | 0.009 | 0.60115 | 18000 | 0.00010973
1.2e-06 | 353867.6726 | 5e-08 | 7705472.0254 | 1.2e-06 | 642428.5484 | 0.01 | 0.8604 | 18500 | 0.00010375
1.3e-06 | 294761.2612 | 6e-08 | 7084373.9572 | 1.3e-06 | 601113.4738 | 0.0125 | 1.7727 | 19000 | 9.6483e-05
1.4e-06 | 244074.5513 | 7e-08 | 6422239.2353 | 1.4e-06 | 552529.9507 | 0.015 | 3.0624 | 19500 | 8.8374e-05
1.5e-06 | 201072.7109 | 8e-08 | 5762276.0472 | 1.5e-06 | 500139.0981 | 0.0175 | 4.684 | 20000 | 7.9821e-05
1.6e-06 | 164910.864 | 9e-08 | 5129581.4213 | 1.6e-06 | 446706.5178 | 0.02 | 6.5525 | 21000 | 6.2704e-05
1.7e-06 | 134724.2007 | 1e-07 | 4538081.3809 | 1.7e-06 | 394325.0956 | 0.0225 | 8.5609 | 22000 | 4.7128e-05
1.8e-06 | 109682.3154 | 2e-07 | 1113020.9662 | 1.8e-06 | 344485.1303 | 0.025 | 10.5966 | 23000 | 3.4105e-05
1.9e-06 | 89019.4928 | 3e-07 | 236409.5643 | 1.9e-06 | 298166.6594 | 0.0275 | 12.5538 | 24000 | 2.3891e-05
2e-06 | 72049.1598 | 4e-07 | 47342.4227 | 2e-06 | 255937.295 | 0.03 | 14.3423 | 25000 | 1.6274e-05
2.1e-06 | 58168.2007 | 5e-07 | 9179.5534 | 2.1e-06 | 218045.3276 | 0.0325 | 15.8919 | 26000 | 1.082e-05
2.2e-06 | 46855.0522 | 6e-07 | 1743.9268 | 2.2e-06 | 184502.4998 | 0.035 | 17.1546 | 27000 | 7.0455e-06
2.3e-06 | 37664.2212 | 7e-07 | 326.6764 | 2.3e-06 | 155154.0199 | 0.0375 | 18.1033 | 28000 | 4.5054e-06
2.4e-06 | 30218.9804 | 8e-07 | 60.5661 | 2.4e-06 | 129735.4197 | 0.04 | 18.7303 | 29000 | 2.8363e-06
2.5e-06 | 24203.378 | 9e-07 | 11.1409 | 2.5e-06 | 107917.0771 | 0.0425 | 19.0434 | 30000 | 1.7615e-06
2.6e-06 | 19354.2673 | 1e-06 | 2.0367 | 2.6e-06 | 89337.8515 | 0.045 | 19.0631 | 31000 | 1.0813e-06
2.7e-06 | 15453.7741 | 2e-06 | 7.0891e-08 | 2.7e-06 | 73629.5361 | 0.0475 | 18.8188 | 32000 | 6.5705e-07
2.8e-06 | 12322.4265 | 3e-06 | 2.137e-15 | 2.8e-06 | 60433.8382 | 0.05 | 18.3455 | 33000 | 3.9579e-07
2.9e-06 | 9813.041 | 4e-06 | 6.0734e-23 | 2.9e-06 | 49413.4741 | 0.0525 | 17.6812 | 34000 | 2.3664e-07
3e-06 | 7805.3841 | 5e-06 | 1.6713e-30 | 3e-06 | 40258.7672 | 0.055 | 16.8644 | 35000 | 1.4058e-07
3.1e-06 | 6201.5769 |  |  | 3.1e-06 | 32690.9168 | 0.0575 | 15.9324 | 40000 | 9.7334e-09
3.2e-06 | 4922.1838 |  |  | 3.2e-06 | 26462.8897 | 0.06 | 14.9202 | 50000 | 4.1526e-11
3.3e-06 | 3902.9159 |  |  | 3.3e-06 | 21358.6826 | 0.0625 | 13.8591
3.4e-06 | 3091.8726 |  |  | 3.4e-06 | 17191.537 | 0.065 | 12.7765
3.5e-06 | 2447.2488 |  |  | 3.5e-06 | 13801.5353 | 0.0675 | 11.696
3.6e-06 | 1935.4412 |  |  | 3.6e-06 | 11052.8959 | 0.07 | 10.6367
3.7e-06 | 1529.4899 |  |  | 3.7e-06 | 8831.1866 | 0.0725 | 9.6139
3.8e-06 | 1207.8024 |  |  | 3.8e-06 | 7040.6052 | 0.075 | 8.6392
3.9e-06 | 953.1129 |  |  | 3.9e-06 | 5601.4225 | 0.0775 | 7.721
4e-06 | 751.6352 |  |  | 4e-06 | 4447.6418 | 0.08 | 6.8648
4.1e-06 | 592.3773 |  |  | 4.1e-06 | 3524.8992 | 0.0825 | 6.0738
4.2e-06 | 466.5855 |  |  | 4.2e-06 | 2788.6135 | 0.085 | 5.3491
4.3e-06 | 367.2974 |  |  | 4.3e-06 | 2202.3743 | 0.0875 | 4.69
4.4e-06 | 288.9811 |  |  | 4.4e-06 | 1736.5572 | 0.09 | 4.0949
4.5e-06 | 227.2462 |  |  | 4.5e-06 | 1367.1429 | 0.0925 | 3.5609
4.6e-06 | 178.6115 |  |  | 4.6e-06 | 1074.7197 | 0.095 | 3.0846
4.7e-06 | 140.3191 |  |  | 4.7e-06 | 843.6466 | 0.0975 | 2.6622
4.8e-06 | 110.1863 |  |  | 4.8e-06 | 661.3571 | 0.1 | 2.2895
4.9e-06 | 86.4868 |  |  | 4.9e-06 | 517.7807 | 0.125 | 0.42765
5e-06 | 67.8565 |  |  | 5e-06 | 404.8675 | 0.15 | 0.062088
5.1e-06 | 53.218 |  |  | 5.1e-06 | 316.1978 | 0.175 | 0.0073642
5.2e-06 | 41.7214 |  |  | 5.2e-06 | 246.6628 | 0.2 | 0.00073347
5.3e-06 | 32.6964 |  |  | 5.3e-06 | 192.2058 | 0.225 | 6.2302e-05
5.4e-06 | 25.6144 |  |  | 5.4e-06 | 149.6117 | 0.25 | 4.5509e-06
5.5e-06 | 20.0595 |  |  | 5.5e-06 | 116.3369 | 0.275 | 2.8689e-07
5.6e-06 | 15.7041 |  |  | 5.6e-06 | 90.373 | 0.3 | 1.5612e-08
5.7e-06 | 12.2905 |  |  | 5.7e-06 | 70.1366 | 0.325 | 7.3166e-10
5.8e-06 | 9.6159 |  |  | 5.8e-06 | 54.3813 | 0.35 | 2.9394e-11
5.9e-06 | 7.5211 |  |  | 5.9e-06 | 42.1276 | 0.375 | 1.0057e-12
6e-06 | 5.8809 |  |  | 6e-06 | 32.6069 | 0.4 | 2.9057e-14
6.1e-06 | 4.5972 |  |  | 6.1e-06 | 25.2169 | 0.425 | 7.0157e-16
6.2e-06 | 3.5927 |  |  | 6.2e-06 | 19.486 | 0.45 | 1.398e-17
6.3e-06 | 2.807 |  |  | 6.3e-06 | 15.0457 | 0.475 | 2.2649e-19
6.4e-06 | 2.1925 |  |  | 6.4e-06 | 11.6085 | 0.5 | 2.9317e-21
6.5e-06 | 1.7122 |  |  | 6.5e-06 | 8.95
6.6e-06 | 1.3367 |  |  | 6.6e-06 | 6.8954
6.7e-06 | 1.0434 |  |  | 6.7e-06 | 5.3088
6.8e-06 | 0.81422 |  |  | 6.8e-06 | 4.0846
6.9e-06 | 0.63526 |  |  | 6.9e-06 | 3.1406
7e-06 | 0.49553 |  |  | 7e-06 | 2.4133
7.1e-06 | 0.38645 |  |  | 7.1e-06 | 1.8532
7.2e-06 | 0.30133 |  |  | 7.2e-06 | 1.4223
7.3e-06 | 0.23491 |  |  | 7.3e-06 | 1.091
7.4e-06 | 0.18309 |  |  | 7.4e-06 | 0.83635
7.5e-06 | 0.14268 |  |  | 7.5e-06 | 0.6408
7.6e-06 | 0.11117 |  |  | 7.6e-06 | 0.49071
7.7e-06 | 0.086603 |  |  | 7.7e-06 | 0.37558
7.8e-06 | 0.067453 |  |  | 7.8e-06 | 0.28731
7.9e-06 | 0.052529 |  |  | 7.9e-06 | 0.21968
8e-06 | 0.040901 |  |  | 8e-06 | 0.16789
8.1e-06 | 0.031842 |  |  | 8.1e-06 | 0.12825
8.2e-06 | 0.024785 |  |  | 8.2e-06 | 0.097925
8.3e-06 | 0.01929 |  |  | 8.3e-06 | 0.074736
8.4e-06 | 0.01501 |  |  | 8.4e-06 | 0.057014
8.5e-06 | 0.011679 |  |  | 8.5e-06 | 0.043476
8.6e-06 | 0.0090855 |  |  | 8.6e-06 | 0.033138
8.7e-06 | 0.007067 |  |  | 8.7e-06 | 0.025249
8.8e-06 | 0.0054962 |  |  | 8.8e-06 | 0.01923
8.9e-06 | 0.0042741 |  |  | 8.9e-06 | 0.01464
9e-06 | 0.0033232 |  |  | 9e-06 | 0.011141
9.1e-06 | 0.0025836 |  |  | 9.1e-06 | 0.0084759
9.2e-06 | 0.0020084 |  |  | 9.2e-06 | 0.0064457
9.3e-06 | 0.001561 |  |  | 9.3e-06 | 0.0049
9.4e-06 | 0.0012132 |  |  | 9.4e-06 | 0.0037237
9.5e-06 | 0.00094271 |  |  | 9.5e-06 | 0.0028289
9.6e-06 | 0.00073248 |  |  | 9.6e-06 | 0.0021483
9.7e-06 | 0.00056906 |  |  | 9.7e-06 | 0.001631
9.8e-06 | 0.00044206 |  |  | 9.8e-06 | 0.0012378
9.9e-06 | 0.00034337 |  |  | 9.9e-06 | 0.00093914
1e-05 | 0.00026668 |  |  | 1e-05 | 0.00071231
2e-05 | 2.0595e-15 |  |  | 2e-05 | 2.7561e-16
3e-05 | 1.1929e-26 |  |  | 3e-05 | 4.4988e-29
4e-05 | 6.1415e-38 |  |  | 4e-05 | 5.1575e-42
5e-05 | 2.9643e-49 |  |  | 5e-05 | 4.872e-55
6e-05 | 1.3736e-60 |  |  | 6e-05 | 4.0717e-68
7e-05 | 6.1878e-72 |  |  | 7e-05 | 3.1272e-81
8e-05 | 2.7307e-83 |  |  | 8e-05 | 2.2577e-94